CENWP-OP-B                                                                                                                                     02 May 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 18 of 2004, which covers the period 25 April through 01 May 2004.

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 188.2 to 204.6 kcfs.  Daily project tailwater elevation averaged 14.6’ to 15.6’ msl.  Daily project forebay elevation averaged 73.0’ to 75.8’ msl.  Daily river temperature averaged 51 to 52° F.  Daily turbidity measured 4.0 to 7.0 on the secchi disk.  

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 85.5 to 93.4 kcfs.   See misc. 6.2 and 6.5
1.3 Unit operation.

1.3.1 Unit 0 was out of service from 1238 until 1419 on 26 April due to governor low oil pressure.    

1.3.2 Unit 1 remains out of service for turbine rehab.

1.3.3 Unit 11 had a 1% violation from 0723 until 0827 on 26 April due to STS inspections.

1.3.4 Unit 12 had a 1% violation from 0827 until 0917 on 26 April due to STS inspections. 

1.3.5 Unit 13 had a 1% violation from 0958 until 1055 on 26 April due to STS inspections.

1.3.6 Unit 14 had a 1% violation from 1055 until 1205 on 26 April due to STS inspections.

1.3.7 Unit 15 went to manual 3D cam adjustment at 0933 on 05 April.  The cam was automatically adjusting and draining power which led to a governor lock up and complete loss of control.  New modules are on order.   

1.3.8 Unit 15 had a 1% violation from 1235 until 1421 on 26 April due to STS inspections.

1.3.9 Unit 16 had a 1% violation from 1456 until 1610 on 26 April due to STS inspections. 

1.3.10 Unit 17 was out of service from 0407 on 26 April until 1546 on 27 April to repair servo motor.

1.3.11 Unit 18 had a 1% violation from 1021 until 1115 on 27 April due to STS inspections.  

1.3.12 Fish Unit 1 (FI) was out of service from 0214 until 0700 on 29 April because the field breaker would not close.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES. 
2.1 AWS Closures.  No AWS valves were closed this reporting week.

2.2 STS/VBS Inspections.  

	Unit
	Date
	Run Hours
	Comments

	11
	4/26
	610
	 

	12
	4/26
	642
	

	13
	4/26
	640
	

	14
	4/26
	611
	

	15
	4/26
	618
	

	16
	4/26
	553
	

	17
	4/27
	471
	Video inspection will be conducted 10 May 

	18
	4/27
	636
	


2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week. 

3.  RESEARCH.

3.1 Battelle/BAE Systems FGE testing.  Hydroacoustic installation complete.  Data collection continues.     

3.2 Battelle/BAE Systems Gap Loss Testing.  Scheduled to begin 06 May. 

3.3 CRITFC.  Sampling twice a week.

3.4 ERDC TDG.  Sensors remain installed in the tailrace.

3.5 ODFW Pikeminnow Tagging.  Electrofishing in Bonneville’s forebay and tailrace.

3.6 NOAA FISH lamprey.  Lamprey ladder installation in April.  

3.7 PSMFC SMF.  Nine steelhead, one salmon and two smolts slid over the separator bars this week.  Approximately 270 clipped yearling chinook and 50 clipped steelhead were held for USGS.

3.8 PSMFC PIT tag.  Testing an antenna for the serpentine sections of the fishways.

3.9 USGS FPE testing.  Installation of Radio telemetry equipment complete.  First tagged fish release on 29 April.  

3.10 University of Idaho.  Sampling daily in the AFF.

3.11 Wildlife Services/Avian Abatement.  Birds were hazed this reporting week with rockets, cracker shells, and 15mm pyrotechnics.  None were lethally taken.

3.12 WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS 
4.1 Project biologists inspected 25 April through 01 May this reporting week.  FPC inspected on 26 and 30 April.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 PCC
	Velocity <1.5 fps
	Meter in slowest part of the channel.
	This is a normal condition.
	

	All week
	FG3-4
	Incorrect position for TW
	Bent shaft
	No action taken.
	

	4/26 and 5/1
	PH 2 PCC
	Velocity < 1.5 fps
	Unknown
	
	

	4/28-4/30
	Weirs 37/38
	Weirs reading < > 1.0’
	Unknown
	No action taken.  Only off by about .1’
	

	All week
	Spill bays 1 and 18
	Improper spill gate opening
	Gate hoist malfunction and safety
	See misc. 6.2 
	


4.3 Fish Ladder Temperatures.  .  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Fahrenheit.

	Date
	Wash. Shore
	Bradford Is.

	4/25
	53.5
	53.4

	4/26
	54.1
	54.3

	4/27
	54.4
	54.7

	4/28
	54.2
	54.5

	4/29
	54.4
	54.6

	4/30
	54.5
	54.6

	5/1
	54.7
	54.8


4.4 Sensor Calibration.  Calibration was checked on 29 April this reporting week.

4.5  Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

4.6 Fishway Status.  

4.6.1 DSM1 remains out of service.

4.6.2 On 23 April, the CI fish ladder went to manual due to computer problems.  The ladder remained in criteria.

5 CONSTRUCTION

5.1 PH 2 Corner Collector Hi-Q PIT tag detector- Prototype antenna construction started on Cascades Island.  If feasible, the prototype antenna will then be constructed into the existing channel during the in-water work period during FY05.
5.2 SMF hydrocannons.  The hydro cannons at the SMF are not operational at this time.  The Project is working on repairs.  

5.3 Adult PIT tag exit detectors.  Current schedule is set for installation in both ladders for Winter 04/05.

5.4 Head Gate Delivery.  Off loading of headgates at PH1 is scheduled for 07 June 2004.

5.5 PH 1 Gantry Crane Delivery and Erection.  Scheduled for 9 August through 4 December.    

6 MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

6.1 Sea lions and harbor seals have been observed in the tailrace of both powerhouses and the spillway.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.  

6.2 On 19 April gate hoists for spillbays 1 and 18 were found to be damaged and a safety hazard.  Bays 1 and 18 were dogged off at 2 dogs (2.9 feet).  On 20 April, the bays were dropped to one dog (one foot) in an effort to reduce turbulence at the fishway entrances.  Per a 21 April teletype, spill will be compensated through adjacent bays 2 and 17 and through 3 and 16 in one foot increments.

6.3 On 27 April, the project received a teletype indicating MU4 to be first on and last off to facilitate fish releases for the MGR study.  

6.4 On 30 April, the project received a teletype for a hard constraint forebay elevation of 75-76.5’ msl from 0600 on 4 May until 1800 on 6 May.  This is for the tribal treaty gillnet fishery.

6.5 On 30 April, the Project received the latest teletype for spill.  Nighttime spill levels will be based on minimum discharge expectations.  Day and nighttime spill is detailed in the table below.  

DISCHARGE 
   
DAYTIME      
 
NIGHTTIME

RANGE, KCFS 
 
 KCFS    



 KCFS

125 - 140          

 50            



  50

140 - 160         

 75           


        88

160 - 180          

 75            



110

180 - 230          

 75            



125

        OVER 230 

          
75





GAS CAP

JAMES R. MAHAR, P.E.

Operations Manager

//S//

1
3

