CENWP-OP-B                                                                                                                                     22 June 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 25 of 2004, which covers the period 13 June through 19 June 2004.

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 232.5 to 273.8 kcfs.  Daily project tailwater elevation averaged 17.7’ to 20.0’ msl.  Daily project forebay elevation averaged 75.0’ to 75.7’ msl.  Daily river temperature averaged 57 to 60° F.  Daily turbidity measured 3.5 to 5.0 on the secchi disk.  

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 94.5 to 101.3 kcfs.      BiOp versus 50kcfs testing started on 17 June.  See misc. 6.2
1.3 Unit operation.  

1.3.1 Unit 1 remains out of service for turbine rehab.

1.3.2 Unit 8 had a change in priority to last on, first off.  See misc. 6.1
1.3.3 Unit 15 was out of service from 0703 until 1055 during 16 June for turbine bearing cooling water/cooler work.   Unit 15 went to manual 3D cam adjustment at 0933 on 5 April.  New modules are on order.   

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.
2.  ACTIVITIES. 
2.1 AWS Closures.  The following AWS valves were closed for cleaning.

FV 3-7- closed from 0654 until 0800 on 14 June. 

FV 3-9- closed from 0654 until 0800 on 14 June. 

2.2 STS/VBS Inspections.  The following STSs were inspected this reporting week.

	Unit
	Date
	Run Hours
	Comments

	15
	6/14
	964
	

	16
	6/14
	666
	


Table 1.  STS Inspections.

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week. 

3.  RESEARCH.
3.1 Battelle/BAE Systems FGE testing.  Data collection continues.     

3.2 CRITFC.  Sampling twice a week.

3.3 ERDC TDG.  Sensors remain installed in the tailrace.

3.4 ODFW Pikeminnow Tagging.  Electrofishing in Bonneville’s forebay and tailrace will continue on 28 June through 2 July.

3.5 NOAA FISH lamprey.  Lamprey ladder installation began 24 May.  

3.6 Pelfrey’s Sturgeon Hatchery.  Capturing breeding size sturgeon in Bonneville’s tailrace daily from 5/28 – 6/28.

3.7 PSMFC SMF.  Six steelhead and two salmon were observed sliding over the separator bars this week.     

3.8 USGS FPE testing.  Summer study to begin 20 June.  

3.9 University of Idaho.  Sampling daily in the AFF.

3.10 Wildlife Services/Avian Abatement.  Birds were hazed this reporting week with rockets, cracker shells, and 15mm pyrotechnics.  None were lethally taken.

3.11 WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS 
4.1 Project biologists inspected 13 June through 19 June this reporting week.      

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 PCC
	Velocity <1.5 fps
	Meter in slowest part of the channel
	This is a normal condition.
	

	All week
	FG3-4
	Incorrect position for TW
	Bent shaft
	No action taken.
	

	All week
	PH2 PCC
	Velocity < 1.5 fps
	No acoustic sensor
	Will repair during winter 04/05
	

	All week
	Cascades Island 
	In manual
	Computer software issue
	TR submitted 

See  4.6.1
	04-21382


4.3 Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Fahrenheit.

	Date
	Wash. Shore
	Bradford Is.

	6/13
	59.9
	59.9

	6/14
	59.8
	59.9

	6/15
	60.0
	60.2

	6/16
	60.4
	60.5

	6/17
	61.3
	61.3

	6/18
	62.0
	62.1

	6/19
	62.5
	62.6


4.4 Sensor Calibration.  Calibration was checked on 18 June this reporting week.

4.5  Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

4.6 Fishway Status.  

4.6.1 Cascade Island has not been properly controlling in Auto all week due to a software issue.    TR has been submitted and electricians are troubleshooting the system.     

5 CONSTRUCTION

5.1 PH 2 Corner Collector Hi-Q PIT tag detector- PIT antenna scheduled for delivery at PH 2 forebay on 25 June.  If feasible, the prototype antenna will then be constructed into the existing channel during the in-water work period during FY05.  
5.2 SMF hydrocannons.  The hydro cannons at the SMF are not operational at this time.  Repairs to the avian cannon are scheduled for completion by the end of June.  Wildlife services will conduct full time hazing activities until 26 June.   

5.3 Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

5.4 PH 1 Gantry Crane Delivery and Erection.  Scheduled for 9 August through 4 December.    

6 MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

6.1 On 17 June, a teletype was sent changing Unit 8 to a last on, first off unit from 17-23 June.  This change is needed to facilitate the trashrack replacement scheduled for the week of 21 June.

6.2 On 17 June, a new spill teletype was sent, detailing the dates for BiOp (75kcfs) and 50kcfs spill.  The pre-test started on 17 June.  The testing period is from 20 June through 07 August.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1
2

