CENWP-OP-B                                                                                                                                     9 August 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 32 of 2004, which covers the period from 01 through 07 August 2004.

1.  OPERATION SUMMARY

1.1 Daily river flow averaged 126.6 to 157.4 kcfs.  Daily project tailwater elevation averaged 9.9’ to 12.6’ msl.  Daily project forebay elevation averaged 74.9’ to 75.8’ msl.  Daily river temperature averaged 69 to 70°F.  Daily turbidity measured 5.0 to 7.0 on the secchi disk.  

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 84.7 to 94.2 kcfs.  Control room indications do not reflect actual flow through the main dam.  Corrective actions are being coordinated at this time.

1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 1 remains out of service for turbine rehab.

1.3.3 Unit 11 had a 1% violation on 04 August due to STS inspections.

1.3.4 Unit 12 had a 1% violation on 05 August due to STS inspections.

1.3.5 Unit 13 had a 1% violation on 05 August due to STS inspections.

1.3.6 Unit 15 went out of service at 0520 on 02 August for annual maintenance and brake repairs.  Unit 15 remains on manual 3D cam adjustment.  New modules are on order. 

1.3.7 Unit 16 was out of service from 0520 on 02 August until 1435 on 05 August for annual maintenance.  Unit 16 was ran out of FPP priority from 1736 until 2000 on 05 August to test the T-12.

1.3.8 Unit 17 was out of service from 0520 on 02 August until 1418 on 05 August for annual maintenance.  Unit 17 was out of service from 1618 until 1730 on 05 August due to the T-12 tripping.

1.3.9 Unit 18 remains out of service for 4-year overhaul.   

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.   Both Fish Units were on standby from 0810 until 1040 to facilitate the ROV inspection of the Washington Shore fishway.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week:

2.1.1 FV1-1- closed from 0725 until 1210 on 03 August to facilitate the ROV inspection of the PH1 PCC.

2.1.2 FV3-9- closed from 0725 until 1527 on 03 August to facilitate the ROV inspection of the PH1 PCC and B-Branch entrance.

2.1.3 FV3-7- closed from 0725 until 1210 on 03 August to facilitate the ROV inspection of the PH1 PCC.

2.1.4 FV4-4- closed from 1210 until 1527 on 03 August to facilitate the ROV inspection of the B-Branch entrance. 

2.1.5 FV5-3/5-4- closed from 1120 until 1220 on 04 August to facilitate the ROV inspection of the Cascades Island fishway entrance.

2.1.6 FV5-9- closed from 1120 until 1220 on 04 August to facilitate the ROV inspection of the Cascades Island fishway entrance.

2.1.7 FV6-9- closed from 0752 until 1035 on 04 August to facilitate the ROV inspection of the Washington Shore fishway.

2.2 STS/VBS Inspections.    No STS/VBS inspections were conducted this week. 

2.3 Dewatering and Fish Salvage.  Unit 15 taillogs were pulled on 04 August.  One sculpin was released back to the river. 
3.  RESEARCH
3.1 CRITFC.  Due to water temperatures over 72º F, no sampling was conducted this reporting week.

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA FISH lamprey.  Lamprey tagging continues.  

3.4 PSMFC SMF.  No salmonids were observed sliding over the separator bars this week.   

3.5 Univ. of Idaho.   Due to water temperatures over 72º F, no sampling was conducted this reporting week.

3.6 WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS

4.1 Project biologists inspected 01 through 07 August this reporting week.  

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 PCC
	Velocity <1.5 fps
	Meter in slowest part of the channel
	This is a normal condition.
	

	All week
	PH2 PCC
	Velocity < 1.5 fps
	No acoustic sensor
	Will repair during winter 04/05
	

	8/1-5
	PH1 ITS chaingates
	Chaingates were not at the correct elevation.
	Removal of research equipment.
	Riggers reset gates to correct levels.
	

	8/2, 8/5
	Weir 37 and 38
	Reading <1.3’>
	Unknown
	
	

	8/3
	BI A and B branches
	Water levels low
	ROV inspection of the fishways.
	Everything back to normal by 1600.
	

	8/4
	Washington Shore
	Water levels low
	ROV inspection of the fishway.
	Everything back to normal by 1200
	

	8/4
	Cascades Island
	Water levels low
	ROV inspection of the fishway.
	Everything back to normal by 1300.
	


4.3 Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Measurements for the AFF are taken in the exit ladder.  Temperatures are in Fahrenheit.

	Date
	Wash. Shore daily average
	Bradford Is. daily average
	AFF exit daily maximum

	8/01
	72.4
	72.6
	72.6

	8/02
	72.3
	72.3
	72.6

	8/03
	72.0
	72.0
	72.1

	8/04
	72.3
	72.3
	72.6

	8/05
	72.4
	72.4
	72.6

	8/06
	72.3
	72.2
	72.4

	8/07
	72.0
	72.1
	72.2


4.4 Sensor Calibration.  Calibration was checked on 02 August this reporting week.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 PH 2 Corner Collector Hi-Q PIT tag detector.  Tests are not proving feasible.  Development of the final antenna and contract has been halted. 
5.2 Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

5.3 PH 1 Gantry Crane Delivery and Erection.  Scheduled for 9 August through 4 December.    

6.  MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

6.1 Cascades Island fishway computer remains in manual due to failure to properly control.

6.2 On 03 August, USGS had the anchors and floats removed from the PH1 tailrace.

6.3 On 03-04 August, mid season fishway inspections were conducted with an ROV instead of divers.  Results are favorable to this type of routine inspection.  Please contact Bonneville Fisheries for a copy of the inspection and examples of sonar images. 

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1
3

