CENWP-OP-B                                                                                                                                     16 August 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 33 of 2004, which covers the period from 08 through 14 August 2004.

1.  OPERATION SUMMARY

1.1 Daily river flow averaged 123.8 to 181.3 kcfs.  Daily project tailwater elevation averaged 9.3’ to 13.6’ msl.  Daily project forebay elevation averaged 74.2’ to 75.6’ msl.  Daily river temperature averaged 69 to 72°F.  Daily turbidity measured 5.0 to 7.0 on the secchi disk.  

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 81.2 to 97.6 kcfs.  Control room indications do not reflect actual flow through the main dam.  Corrective actions are being coordinated at this time.  See misc. 6.1
1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 1 remains out of service for turbine rehab.

1.3.3 Unit 6 was out of service from 1326 until 1630 on 10 August to raise and lower contacts on generator breaker.  

1.3.4 Unit 12 was out of service from 1306 on 09 August until 1536 on 10 August due to a smoked brake solenoid.

1.3.5 Unit 15 was out of service from 0520 on 02 August until 1616 on 09 August for annual maintenance and brake repairs.  

1.3.6 Unit 17 had a 1% violation on 09 August from 1411-1604 due to STS camera inspection.  

1.3.7 Unit 18 remains out of service for 4-year overhaul.   

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.   

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed this reporting week. 

2.2 STS/VBS Inspections.    The following STSs were inspected this reporting week.  

	Unit
	Date
	Run Hours
	Comments

	11
	8/4
	641
	

	12
	8/5
	739
	

	13
	8/5
	650
	

	14
	8/9
	587
	

	15
	8/9
	400
	

	16
	8/9
	265
	

	17
	8/9
	927
	

	18
	7/1
	369
	Out of Service


Table 1.  STS Inspections.
2.3 Dewatering and Fish Salvage. No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 CRITFC.  Due to water temperatures over 72º F, no sampling was conducted this reporting week.

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA FISH lamprey.  Lamprey tagging continues.  

3.4 PSMFC SMF.  No salmonids were observed sliding over the separator bars this week.   

3.5 Univ. of Idaho.   Due to water temperatures over 72º F, no sampling was conducted this reporting week.

3.6 WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS

4.1 Project biologists inspected 08 through 14 August this reporting week.  

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 PCC
	Velocity <1.5 fps
	Meter in slowest part of the channel
	This is a normal condition.
	

	All week
	PH2 PCC
	Velocity < 1.5 fps
	No acoustic sensor
	Will repair during winter 04/05
	

	8/10
	B-branch
	Tailwater/Entrance differential too high
	Entrance Cpu sensor read 0.6 ft too high
	Adjusted in manual

See misc. 6.2
	

	8/10
	Cascades Island
	Tailwater/Entrance differential too high
	Tailwater Cpu sensor read 0.5 ft too high
	Adjusted in manual

See misc. 6.2
	


4.3 Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Measurements for the AFF are taken in the exit ladder.  Temperatures are in Fahrenheit.

	Date
	Wash. Shore daily average
	Bradford Is. daily average
	AFF exit daily maximum

	8/08
	72.3
	72.1
	72.4

	8/09
	72.3
	72.3
	72.5

	8/10
	73.1
	73.0
	73.2

	8/11
	73.7
	73.7
	73.8

	8/12
	74.2
	74.1
	74.3

	8/13
	74.4
	74.4
	74.5

	8/14
	74.1
	74.3
	74.3


4.4 Sensor Calibration.  Calibration was checked on 14 August this reporting week.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 PH 2 Corner Collector Hi-Q PIT tag detector.  Tests are not proving feasible.  Development of the final antenna and contract has been halted. 
5.2 Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

5.3 PH 1 Gantry Crane Delivery and Erection.  Scheduled for 9 August through 4 December.    

6.  MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS
6.1  On 09 August, the Project received the latest teletype for spill.  Increase each spill bay opening by 0.3 foot over the opening shown in the Fish Passage Plan during daytime and minimum spill periods to meet BiOp spill requirements.  
6.2 B-Branch and Cascades Island fishway computers remain in manual due to failure to properly control.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1
2

