CENWP-OP-B                                                                                                                                     30 August 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 35 of 2004, which covers the period from 22 through 28 August 2004.

1.  OPERATION SUMMARY

1.1 Daily river flow averaged 130.1 to 184.3 kcfs.  Daily project tailwater elevation averaged 10.3’ to 14.4’ msl.  Daily project forebay elevation averaged 75.2’ to 75.9’ msl.  Daily river temperature averaged 68 to 71°F.  Daily turbidity measured 4.5 to 6.8 on the secchi disk.  

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 87.3 to 112.3 kcfs.  Control room indications do not reflect actual flow through the main dam.  Corrective actions are being coordinated at this time.  See misc. 6.1
1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 1 remains out of service for turbine rehab.

1.3.3 Units 9 and 10 went out of service at 0500 on 24 August to facilitate gantry crane three construction.

1.3.4 Unit 11 was out of service from 0400 on 23 August until 1501 on 26 August for annual maintenance.

1.3.5 Unit 12 went out of service at 0400 on 23 August for annual maintenance.

1.3.6 Unit 13 was out of service from 0400 on 23 August until 1501 on 26 August for annual maintenance.

1.3.7 Unit 14 went out of service at 0400 on 23 August for annual maintenance.  

1.3.8 Unit 17 was out of service from 0423 until 0436 on 23 August due to a tripped breaker.

1.3.9 Unit 18 remains out of service for 4-year overhaul.   

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.   

1.4.1 F1 was out of service from 0421 until 0509 on 23 August for station service transfer.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week. 

FV1-1 closed for cleaning from 1014 until 1022 on 26 August.

2.2 STS/VBS Inspections.    No STSs/VBSs were inspected this reporting week.  

2.3 Dewatering and Fish Salvage. The following dewatering or salvage activities occurred this reporting week.  
2.3.1 Unit 14 tail logs were pulled on 26 August.  
3.  RESEARCH
3.1 CRITFC.  Sampled on Tuesday and Friday this reporting week.  Temperatures dropped below 72ºF. 

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA FISH lamprey.  Lamprey tagging continues.  

3.4 PSMFC SMF.  No salmonids were observed sliding over the separator bars this week.   

3.5 Univ. of Idaho.   Sampled on Tuesday and Friday this reporting week.  Temperatures dropped below 72ºF.

3.6 WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS

4.1 Project biologists inspected 22 through 28 August this reporting week.  

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 PCC
	Velocity <1.5 fps
	Meter in slowest part of the channel
	This is a normal condition.
	

	All week
	PH2 PCC
	Velocity < 1.5 fps
	No acoustic sensor
	Will repair during winter 04/05
	

	8/22
	A branch
	Water elevations >1.0’
	Still in shad passage mode.
	Electricians adjusted fishways on 8/22
	

	8/22
	Cascades Island UMT
	Water elevations >1.0’
	Still in shad passage mode.
	Electricians adjusted fishways on 8/22
	


4.3 Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Measurements for the AFF are taken in the exit ladder.  Temperatures are in Fahrenheit.

	Date
	Wash. Shore daily average
	Bradford Is. daily average
	AFF exit daily maximum

	8/22
	73.5
	73.3
	73.6

	8/23
	72.8
	72.7
	72.9

	8/24
	72.4
	72.2
	72.5

	8/25
	71.4
	71.1
	71.6

	8/26
	71.2
	70.8
	71.4

	8/27
	71.2
	71.0
	71.4

	8/28
	71.6
	71.4
	71.8


4.4 Sensor Calibration.  Calibration was checked on 27 August this reporting week.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

5.2 PH 1 Gantry Crane Delivery and Erection.  Construction will continue through 04 December.    

6.  MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS
6.1  On 09 August, the Project received the latest teletype for spill.  Increase each spill bay opening by 0.3 foot over the opening shown in the Fish Passage Plan during daytime and minimum spill periods to meet BiOp spill requirements.  
6.2 A teletype issued on 19 August requests a flow restriction not to exceed 150 Kcfs from 0700 until 1130 on 06 September.  This is to reduce currents in the river for the cross channel swim at Hood River.

6.3 A teletype issued on 25 August requests a hard forebay constraint of 75.0- 76.5’ from 0600 on 31 August until 1800 on 03 September.  This restriction is to accommodate the treaty gill net fishing.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1
2

