CENWP-OP-B                                                                                                                                  19 September 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 38 of 2004, which covers the period from 12 through 18 September 2004.

1.  OPERATION SUMMARY

1.1 Daily river flow averaged 89.5 to 115.4 kcfs.  Daily project tailwater elevation averaged 9.7’ to 11.3’ msl.  Daily project forebay elevation averaged 73.2’ to 76.0’ msl.  Daily river temperature averaged 64 to 66°F.  Daily turbidity measured 6.0 to 7.0 on the secchi disk.  

1.2 Spill Bays 1 and 18, which supply adult attraction flow for Cascades Island and B Branch respectively, are open during daylight hours (0500 until 1930).  Spill averaged 2.2 to 2.4 kcfs.  

1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 1 remains out of service for turbine rehab.

1.3.3 Unit 2 was out of service from 0411 until 1551 on 14 September for phase testing on Unit 1.  Unit 2 was also out of service from 1033 until 1623 on 15 September for STS/VBS installation.

1.3.4 Unit 3 was out of service from 0644 until 1029 on 15 September for STS/VBS installation.

1.3.5 Units 9 and 10 remain out of service for gantry crane three construction.

1.3.6 Unit 11 was out of service from 0747 until 1337 on 16 September for antenna repairs on the STSs.

1.3.7 Unit 18 remains out of service for 4-year overhaul.   

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.   

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed this reporting week. 

2.2 STS/VBS Inspections.  The following STSs/VBSs were installed this reporting week.  

	Unit
	Date
	Run Hours
	Comments

	2
	9/15
	
	

	3
	9/15
	
	


Table 1.  STS/VBS Inspections.

2.3 Dewatering and Fish Salvage. No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 Battelle.  Currently scheduled to remove the B2CC barge on 21 September.  Spill gate antennas removed earlier this month.

3.2 CRITFC.  Sampling continues twice a week. 

3.3 ERDC TDG.  Sensors remain installed in the tailrace.

3.4 NOAA FISH lamprey.  Removal of the lamprey ladder at Bradford Island was completed by 15 September.

3.5 PSMFC SMF.  Six salmon were observed sliding over the separator bars this week.   

3.6 Univ. of Idaho.  Tagging continues.  Antennas were removed from the main dam tailrace on 14 September.

3.7 USGS.  Removed antennas from main dam.  Repaired antennas on Unit 11 STSs.

3.8 WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

3.9 WDFW/ODFW.  Tule counting started on 15 August and will continue until 15 October.

4.  FISHWAYS

4.1 Project biologists and FFU inspected 12 through 18 September this reporting week.  

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 PCC
	Velocity <1.5 fps
	Meter in slowest part of the channel
	This is a normal condition.
	

	All week
	PH2 PCC
	Velocity < 1.5 fps
	No acoustic sensor
	Will repair during winter 04/05
	

	9/18
	Cascades Island
	Diffusers and differential
	Unknown
	Operators put fishway in manual.  See 6.1.2
	TR submitted on 9/19


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Measurements for the AFF are taken in the exit ladder.  Temperatures are in Fahrenheit.

	Date
	Wash. Shore daily average
	Bradford Is. daily average
	AFF exit daily maximum

	9/12
	68.7
	68.7
	68.8

	9/13
	68.1
	67.9
	68.3

	9/14
	67.4
	67.2
	67.6

	9/15
	67.4
	67.3
	67.5

	9/16
	67.1
	67.0
	67.2

	9/17
	66.7
	66.5
	66.7

	9/18
	66.3
	66.1
	66.4









Table 3.  Fishway Temperatures.

4.4 Sensor Calibration.  Calibration was checked on 16 September this reporting week.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

5.2 PH 1 Gantry Crane Delivery and Erection.  Construction will continue through 04 December.    

6.  FISHWAY STATUS

6.1 Adult Fishways.  

6.1.1 As per the FPP, two priority units were operated at PH1 when fish numbers met or exceeded 25,000 fish.  This unit operation will continue until fish numbers drop below 25,000.

6.1.2 Cascades Island computer is not controlling properly.  The fishway is currently in manual operation and maintaining criteria.  Operators will submit a TR.

6.2 Juvenile Fishways.

6.2.1 DSM1

6.2.1.1 DSM 1 started running south at 1710 on 15 September.  All orifices are open and lights are on in Units 2 and 3.

6.2.2 DSM2.  

6.2.2.1 F2 manual orifices were closed on 16 September.  

6.2.2.2 The mechanical screen cleaners were exercised on 13 September.

7.  MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS
7.1  A teletype issued on 10 September requests a forebay soft constraint of 75.0’- 76.5’ msl effective at 0700 on 13 September until 1800 on 17 September.  This is to reduce wear and tear on tribal gill net equipment.

7.2 A teletype issued on 17 September requests a forebay hard constraint of 75.0’ – 76.5’ from 0600 on 20 September until 1800 on 24 September.  This is to reduce wear and tear on tribal gill net equipment.

7.3 The winter maintenance schedule is available.  Please contact Fisheries.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1
2

