CENWP-OP-B                                                                                                                                  08 November 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 45 of 2004, which covers the period from 31 October through 06 November 2004.

1.  OPERATION SUMMARY

1.1 Daily river flow averaged 106.8 to 128.6 kcfs.  Daily project tailwater elevation averaged 10.6’ to 12.0’ msl.  Daily project forebay elevation averaged 74.2’ to 75.3’ msl.  Daily river temperature averaged 55 to 58(F.  Daily turbidity measured 7.0 on the secchi disk.  

1.2 Spill Bays 1 and 18, which supply adult attraction flow for Cascades Island and B Branch respectively, are open during daylight hours (0500 until 1930).  Spill averaged 2.2 to 2.3 kcfs.  

1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 1 was out of service from 0738 on 01 November until 1720 on 02 November for breaker repair.

1.3.3 Unit 2 remains out of service for turbine rehab.

1.3.4 Unit 9 was out of service from 0738 on 01 November until 1720 on 02 November for Unit 1 breaker repair.

1.3.5 Unit 10 remains out of service for gantry crane three construction.

1.3.6 Unit 15 was out of service from 1857 on 31 October until 1407 on 02 November due to inability to control governor.   

1.3.7 Unit 18 remains out of service for 4-year overhaul.   

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.   

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed for cleaning this reporting week.

2.1.1 FV 1-1- from 0717 until 0730 on 01 November.  

2.2 STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week. 

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 USGS.  Monitoring continues.

3.3 WDFW Chum.  Chum trapping and tagging starts 04 November through 22 November.

3.4 WDFW Fish Counting.  Fish counting with video began on 01 November at Washington Shore and Bradford Island.

4.  FISHWAYS

4.1 Project biologists inspected 31 October through 06 November this reporting week.  

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 PCC
	Velocity <1.5 fps
	Meter in slowest part of the channel
	This is a normal condition.
	

	All week
	PH2 PCC
	Velocity < 1.5 fps
	No acoustic sensor
	Will repair during winter 04/05
	

	11/02, 11/05
	Bradford Island fishway
	Both branches and BI weirs reading <1.0’
	Unknown
	
	

	11/04
	Unit 1 and 3 
	Orifice lights out
	Unknown
	Operators corrected
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Fahrenheit.

	Date
	Wash. Shore daily avg.
	Bradford Is. daily avg.

	10/31
	57.2
	56.9

	11/01
	56.7
	56.6

	11/02
	56.4
	56.3

	11/03
	56.1
	56.0

	11/04
	55.0
	55.0

	11/05
	54.2
	54.3

	11/06
	54.1
	54.0


Table 3.  Fishway Temperatures.

4.4 Sensor Calibration.  Calibration was checked on 06 November this reporting week.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 Adult PIT tag exit detectors.  Washington Shore construction to start 29 November.

5.2 PH 1 Gantry Crane Delivery and Erection.  Construction will continue through 04 December.    

5.3 North Monolith repairs.  Plans and specs not yet completed.  Hope to have repairs completed by 28 February.

5.4 B2 Follow on.  Mods to the perf plate and the bypass flume to be completed in February 2005.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Due to the Cascades Island computer not properly controlling, the fishway is now in manual and maintaining criteria.  
6.1.2 Due to the B- Branch computer switching to “lamprey mode”, the fishway in now in manual and maintaining criteria.
6.2 Juvenile Fishways.  

6.2.1  DSM1 continues to run south with STSs and VBSs in Units 1 and 3.
HAZMAT, SPILLS AND CLEANUP
7.  Nothing to report this week.  
8.  MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS
8.1 A teletype issued on 29 October requests a tailwater hard constraint minimum of 10.5’ msl 24 hours a day and between 10.5’ to 12’ msl between 0700 until 1900.  These constraints go into effect starting 01 November and continuing until further notice.  This operation is to maintain water levels over spawning habitat below Bonneville Dam.
JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

