CENWP-OP-B                                                                                                                                  03 January 2005

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 01 of 2005, which covers the period from 26 December 2004 through 01 January 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 125.6 to 153.8 kcfs.  Daily average project tailwater elevation ranged from 12.1’ to 13.7’ msl.  Daily average powerhouse forebay elevation ranged from 73.1’ to 74.2’ msl.  Daily average river temperature remained 46 to 44(F.  Daily turbidity measured 6.0 to 7.0 on the secchi disk.  

1.2 Spill Bay 1, which supplies adult attraction flow for Cascades Island, is open during daylight hours.   Daily average spill ranged from 1.0 to 1.1 kcfs.    

1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 2 remains out of service for turbine rehab.

1.3.3 Unit 10 remains out of service for gantry crane three construction.

1.3.4 Unit 11 remains out of service for unit overhaul.

1.3.5 Unit 18 remains last on first off due to governor trouble.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.4.1 Fish Unit 1 remains out of service for winter maintenance at the Washington Shore fishway.

1.4.2 Fish Unit 2 remains out of service for winter maintenance at the Washington Shore fishway.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves activity occurred this reporting week.

2.1.1 FV1-1- returned to auto at 0420 on 26 December.  Closed to float trash from 1930 on 26 December until 0504 on 27 December and from 0030 until 0510 on 29 December.  

2.1.2 FV3-7- returned to auto at 0420 on 26 December.  Closed to float trash from 1930 on 26 December until 0504 on 27 December and from 0030 until 0510 on 29 December.  Closed for cleaning from 1531 until 1630 on 28 December.

2.1.3 FV3-9- returned to auto at 0420 on 26 December.  Closed to float trash from 1930 on 26 December until 0504 on 27 December and from 0030 until 0510 on 29 December.  

2.1.4 FV 6-9- remains closed.

2.2 STS/VBS Inspections.  STSs/VBSs have been removed until February. 

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 WDFW Fish Counting.  Video counting continues at Bradford Island and Cascades Island.

4.  FISHWAYS

4.1 Project biologists inspected 27-30 December

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	12/27-30
	PH1 WG2
	Opening < 8’
	Unknown
	Adjusted WG 2
	05-10052

	12/28
	FV 3-9 trashrack
	Head diff >FPP criteria
	Aquatic vegetation in the river.
	Riggers raked trashracks.
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are not recorded during the winter maintenance period.

4.4 Sensor Calibration.  Calibration was checked on 28 December this reporting week.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 Adult PIT tag exit detectors.  Washington Shore construction continues.

5.2 PH 1 Gantry Crane Delivery and Erection.  Construction continues.    

5.3 North Monolith repairs.  Plans and specs not yet completed.  

5.4 B2 Follow on.  Mods to the perf plate and the bypass flume to be completed in February 2005.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island fishway is having trouble maintaining proper water elevations due to aquatic vegetation clogging up AWS trashracks.

6.1.2 Cascades Island fishway PLC remains in manual and maintaining criteria.   The exit is open.
6.1.3 Washington Shore fishway, AWS, and AFF remain dewatered.  
6.2 Juvenile Fishways.  

6.2.1 DSM 1 remains dewatered.

6.2.2 DSM2 remains dewatered.

7.  HAZMAT, SPILLS AND CLEANUP- Nothing to report this week.  
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS
8.1 A teletype issued on 22 December switches PH2 unit priority such that Unit 18 is last on first off due to governor problems.

8.2 A teletype issued on 29 December requests a tailwater hard constraint minimum of 11.9’ during all hours.  This operation is to facilitate chum spawning around Ives and Pierce Islands.

8.3 A teletype issued on 29 December requests forebay elevations be maintained between 71.5 – 72.5’ msl as a hard constraint from 0800 until 1700 on 04- 06 January.  This is to facilitate Stevenson boat ramp repairs.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

