CENWP-OP-B                                                                                                                                  24 January 2005

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 04 of 2005, which covers the period from 10 through 22 January 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 128.6 to 148.9 kcfs.  Daily average project tailwater elevation ranged from 12.5’ to 13.9’ msl.  Daily average powerhouse forebay elevation ranged from 74.3’ to 75.5’ msl.  Daily average river temperature averaged 38 to 39(F.  Daily turbidity measured 1.8 to 7.0 on the secchi disk.  

1.2 Spill Bay 1, which supplies adult attraction flow for Cascades Island, is open during daylight hours.   Daily average spill ranged from 0.9 to 1.1 kcfs.    

1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 2 remains out of service for turbine rehab.

1.3.3 Unit 10 remains out of service for gantry crane three construction.

1.3.4 Unit 11 remains out of service for unit overhaul.

1.3.5 Unit 16 was out of service from 0910 until 1648 on 19 January for index testing.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.4.1 Fish Unit 1 remains out of service for winter maintenance at the Washington Shore fishway.

1.4.2 Fish Unit 2 remains out of service for winter maintenance at the Washington Shore fishway.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.
2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves activity occurred this reporting week.

2.1.1 FV1-1- Closed to float trash from 0900 until 1530 on 17 January, closed for cleaning from 0812 until 0845 on 18 January.

2.1.2 FV3-7- Closed for cleaning from 0954 until 1130 on 18 January.

2.1.3 FV3-9- Closed to float trash from 0900 until 1530 on 17 January, closed for cleaning from 0954 until 1130 on 18 January. 

2.1.4 FV 6-9- remains closed.

2.2 STS/VBS Inspections.  STSs/VBSs have been removed until February. 

2.3 Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.  
2.3.1 The north monolith was dewatered on 18 January.  No fish were found.
3.  RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 WDFW Fish Counting.  Video counting continues at Bradford Island and Cascades Island.

4.  FISHWAYS

4.1 Project biologists inspected 18, 20-21 January.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	1/18, 1/21
	BI fishway
	FV3-9 drawdown > .5’
	Aquatic debris
	Riggers cleaned racks.
	

	1/20
	PH1 WG2
	Opening < 8’
	Unknown
	Adjusted WG 2
	05-10052

	1/21
	Cascades Is.
	Exit drawdown >.5’
	Aquatic debris
	Riggers cleaned racks.
	

	
	Bonneville
	No calibration check
	Scheduling 
	
	


Table 2.  FPP Out of Criteria items.
4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are not recorded during the winter maintenance period.

4.4 Sensor Calibration.  Calibration was not checked this reporting week.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 Adult PIT tag exit detectors.  Washington Shore construction continues.

5.2 PH 1 Gantry Crane Delivery and Erection.  Construction continues.    

5.3 North Monolith repairs.  Plans and specs not yet completed.  

5.4 B2 Follow on.  Mods to the perf plate and the bypass flume to be completed in February 2005.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island fishway PLC remains in manual and maintaining criteria.   The Cascades Island exit is open.
6.1.2 A-branch diffusers have been reprogrammed to compensate for FG3-4 being out of service.  FG3-4 will remain out of service until the winter maintenance period 2005/06.
6.1.3 Washington Shore fishway, AWS, and AFF remain dewatered.  
6.2 Juvenile Fishways.  

6.2.1 DSM 1 remains dewatered.

6.2.2 DSM2 remains dewatered.

6.3 Upcoming Events.

6.3.1 Two mile pipe survey tentatively scheduled mid to late January.
7.  HAZMAT, SPILLS AND CLEANUP- Nothing to report this week.  
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS – Nothing to report this week.
JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

