CENWP-OP-B                                                                                                                                  21 February 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 08 of 2005, which covers the period from 13 through 19 February 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 122.1 to 165.0 kcfs.  Daily average project tailwater elevation ranged from 12.3’ to 14.1’ msl.  Daily average powerhouse forebay elevation ranged from 73.7’ to 75.2’ msl.  Daily average river temperature averaged 40 to 41(F.  Daily turbidity measured 5.0 to 7.0 on the secchi disk.  

1.2 Spill Bay 1, which supplies adult attraction flow for Cascades Island, is open during daylight hours.   Daily average spill ranged from 0.9 to 1.3 kcfs.    

1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 1 was out of service from 0805 until 1020 on 15 February for exciter fan maintenance.

1.3.3 Unit 2 remains out of service for turbine rehab.

1.3.4 Unit 10 remains out of service for gantry crane three construction.

1.3.5 Unit 11 was out of service from 1741 on 15 February until 0149 on 16 February due to water in the turbine bearing oil.

1.3.6 Unit 13 was out of service from 0654 on 14 February until 1623 on 15 February for breaker mods.

1.3.7 Unit 15 was out of service from 0730 on 16 February until 1600 on 17 February for breaker mods.

1.3.8 Unit 16 was out of service from 0600 until 1142 on 17 February for trashrack transducer installation.

1.3.9 Unit 17 operated outside the 1% curve from 0846 until 0912 on 14 February to facilitate trashrack raking.  Unit 17 was out of service from 1117 until 1525 on 16 February for transducer installation.

1.3.10 Unit 18 operated outside the 1% curve from 0835 until 0846 on 14 February to facilitate trashrack raking.  Unit 18 was out of service from 0812 until 1106 on 16 February for transducer installation and from 2207 on 16 February until 0317 on 17 February due to timing relay problems.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.4.1 Fish Unit 1 remains out of service for winter maintenance at the Washington Shore fishway.

1.4.2 Fish Unit 2 remains out of service for winter maintenance at the Washington Shore fishway.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves activity occurred this reporting week.

2.1.1 FV1-1- closed for cleaning from 1048 until 1115 on 14 February and from 1500 until 1520 on 16 February.

2.1.2 FV3-7- closed for cleaning from 1500 until 1520 on 16 February.

2.1.3 FV3-9- closed for cleaning from 1030 until 1042 on 14 February and from 1500 until 1520 on 16 February.

2.1.4 FV 6-9- remains closed.

2.2 STS/VBS Inspections.  STSs/VBSs for PH2 have been scheduled for installation the week of 21 February. 

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 Univ. of Idaho.  Installing and repairing antennas in the north monolith and Washington Shore fishway.  Installation of a half duplex PIT tag detector system is scheduled for mid to late February.

3.3 NOAA Fish.  Prototype lamprey flume to be installed 24 February.  Additional installation of above water equipment will occur in April.
3.4 PSMFC.  Smolt monitoring scheduled to begin 01 March.
3.5 USGS FPE and Survival.  Installing radio telemetry equipment.   
3.6 WDFW Fish Counting.  Video counting continues at Bradford Island and Cascades Island.

4.  FISHWAYS

4.1 Project biologists inspected 14, 15, 17, and 18 February.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	2/18
	A-branch
	Water elevation >1.0’
	Unknown
	No action taken
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Temperatures are not recorded during the winter maintenance period.

4.4 Sensor Calibration.  Calibration was checked on 17 February.  PH1 south and central collection channel sensors need to be recalibrated.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 Adult PIT tag exit detectors.  Washington Shore construction to be completed by 28 February.

5.2 PH 1 Gantry Crane Delivery and Erection.  Construction continues.    

5.3 North Monolith repairs.  Construction to be completed by 27 February.

5.4 B2 Follow on.  Mods to the perf plate and the bypass flume completed 19 February.

5.5 B2 VBS modifications.  Gatewell modifications are scheduled to begin in Winter 05/06.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island fishway PLC remains in manual and maintaining criteria.  The Cascades Island exit remains open.
6.1.2 A-branch diffusers have been reprogrammed to compensate for FG3-4 being out of service.  FG3-4 will remain out of service until the winter maintenance period 2005/06.
6.1.3 Washington Shore fishway, AWS, and AFF remain dewatered.  
6.2 Juvenile Fishways.  

6.2.1 DSM 1 remains dewatered.

6.2.2 DSM2 remains dewatered.  Scheduled water up date is 21 February.

6.2.3 SMF hydrocannons are out of service due to shrinkage in the PVC pipes.  New parts are on order.  The booster pump is on order and should be installed by mid March.

6.3 Upcoming Events.

6.3.1 ROV inspection of BI and Cascades Island scheduled for 22 February.
6.3.2 Installation of a guide wall, lamprey flume and half –duplex PIT tag detectors will occur on 24 February at the north monolith NDE.  Divers are expected to complete the work in one day.
6.3.3 Spring Creek is scheduled to release tule chinook on 02 March.
6.3.4 B2CC will be open from 03 through 07 March to facilitate the Spring Creek release.
7.  HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.
8.1 Marine mammals have been observed in the tailrace of Powerhouse One.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.  

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

