CENWP-OP-B                                                                                                                                  13 March 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 11 of 2005, which covers the period from 06 March through 12 March 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 120.4 to 143.7 kcfs.  Daily average project tailwater elevation ranged from 11.5’ to 13.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.9’ to 75.3’ msl.  Daily average river temperature averaged 42 to 44(F.  Daily turbidity measured 6.0 to 7.0 on the secchi disk.  

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 0.5’ during daylight hours.   Daily average spill ranged from 1.2 to 1.3 kcfs.    

1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 2 remains out of service for turbine rehab.

1.3.3 Unit 10 remains out of service for gantry crane three construction.

1.3.4 Unit 12 had a 1% violation on 07 March due to governor alarm troubleshooting activities.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.4.1 Fish Unit 2 was in standby from 1956 until 2008 and from 2012 until 2015 on 10 March to facilitate operator training activities.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed for cleaning this reporting week.

2.2 STS/VBS Inspections.  No STSs/VBSs were installed this reporting week. 

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 Univ of Idaho.  All antennas installed/repaired.  

3.3 NOAA Fish.  Prototype lamprey flume installed.  Installation of above water equipment will occur in April.
3.4 PSMFC.  Nine adult steelhead were seen crossing the separator bars.
3.5 USGS FPE and Survival.  Installing radio telemetry equipment. 
3.6 Battelle FPE and FGE.  Installing hydroacoustic transducers.    
3.7 WDFW Fish Counting.  Video counting continues at Bradford Island and Washington Shore.  Video counting at Cascades Island concluded 07 March.   

4.  FISHWAYS

4.1 Project biologists inspected 06 through 12 March.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Meter not plugged in.
	Electricians working on meter.
	

	3/6-10
	SMF hydrocannons
	Out of service
	Faulty pipe and fittings
	Repairs made on 10 March.
	

	3/11
	CI fishway
	FG6-12 stuck closed
	Bent shaft.
	FG6-11 to compensate
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  

	Date
	Wash. Shore
	Bradford Is.

	3/6
	41.8
	42.2

	3/7
	42.1
	42.4

	3/8
	42.6
	42.9

	3/9
	43.1
	43.4

	3/10
	43.6
	43.9

	3/11
	43.9
	44.2

	3/12
	44.2
	44.6


4.4 Sensor Calibration.  Calibration was checked on 10 March.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 PH 1 Gantry Crane Delivery and Erection.  Construction continues.    

5.2 B2 VBS modifications.  Gatewell modifications are scheduled to begin in Winter 05/06.

5.3 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island fishway PLC are back in manual.  Electricians have determined the problems and are working on corrections.
6.1.2 Cascades Island fishway exit was closed at 1600 on 07 March.  No fish have been seen in the exit section.
6.1.3 A-branch diffusers have been reprogrammed to compensate for FG3-4 being out of service.  FG3-4 will remain out of service until the winter maintenance period 2005/06.
6.1.4 The AFF remains dewatered.  
6.2 Juvenile Fishways.  

6.2.1 DSM 1 remains dewatered.  Chain gates 1C, 3C, and 6C are at 72.0’ msl.  

6.2.2 SMF hydrocannons returned to service at 1525 on 10 March.   The booster pump is on order.

7.  HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.
8.1 A teletype issued on 04 March requests that spill bays 1 and 18 return to normal operation as stated in the FPP, effective 06 March when daytime spill begins.  

8.2 A teletype issued on 11 March requests a hard forebay constraint between 71.5’ – 73.0’ msl, and a soft forebay constraint from 72.5’ – 73.0’ msl, from 0800 until 1700 each day 14-17 March.   This is to facilitate bumper log replacement at the upper navlock entrance.

8.3 Marine mammals have been observed in the tailraces of PH1, PH2 and the Main Dam, the forebay and the Washington shore fishway.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.

8.4 Kelts have been seen holding in the PH1 forebay at chaingate 7A.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

