CENWP-OP-B                                                                                                                                  27 March 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 13 of 2005, which covers the period from 20 March through 26 March 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 118.3 to 144.9 kcfs.  Daily average project tailwater elevation ranged from 11.6’ to 13.1’ msl.  Daily average powerhouse forebay elevation ranged from 74.5’ to 75.7’ msl.  Daily average river temperature averaged 45 to 46(F.  Daily turbidity measured 4.0 to 7.0 on the secchi disk.  

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 0.5’ during daylight hours.   Daily average spill ranged from 1.3 to 1.4 kcfs.    

1.3 Unit operation.  

1.3.1 Unit 0 remains out of service for a 5-year overhaul.

1.3.2 Unit 1 was out of service from 0656 on 24 March until 1720 on 25 March for acceptance testing.

1.3.3 Unit 2 remains out of service for turbine rehab.

1.3.4 Unit 4 was out of service from 0742 until 0831 on 21 March for transducer installation.  Unit 4 had a 1% violation on 25 March due to exciter data collection activities.

1.3.5 Unit 5 was out of service from 0831 until 1127 on 21 March for transducer installation.

1.3.6 Unit 6 was out of service from 1127 until 1526 on 21 March for transducer installation.

1.3.7 Unit 7 was out of service from 1300 until 1534 on 22 March for transducer installation.

1.3.8 Unit 8 was out of service from 1534 until 1603 on 22 March for transducer installation.

1.3.9 Unit 9 was out of service from 1603 until 1640 on 22 March for transducer installation.

1.3.10 Unit 10 remains out of service for gantry crane three construction.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.4.1 F1 was out of service from 1418 until 1606 on 21 March due to governor trouble.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valve activity occurred this reporting week.

2.1.1 FV3-9 - Closed for cleaning from 0702 until 0729 on 22 March.

2.2 STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week. 

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 Univ of Idaho.  All antennas installed/repaired.  

3.3 NOAA Fish.  Prototype lamprey flume installed.  Installation of above water equipment will occur in April.
3.4 PSMFC.  Seven adult steelhead were observed crossing the separator bars this week.  One bull trout was sampled.
3.5 USGS FPE and Survival.  Installing radio telemetry equipment. 
3.6 Battelle FPE and FGE.  Installing hydroacoustic transducers.    
3.7 WDFW Fish Counting.  Video counting continues at Bradford Island and Washington Shore.     

4.  FISHWAYS

4.1 Project biologists inspected 20 through 26 March.  NOAA Fisheries inspected on 24 March.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper installation
	No action taken until S. monolith dewatered.
	

	3/21
	PH2 gatewells
	50% covered with debris
	
	Riggers cleaned gatewells.
	

	3/22
	A-branch
	Staff gauge reading >1.0
	Unknown.  Other gauges in criteria
	No action taken.
	

	3/23-25
	FG6-12
	incorrect position for TW elevation.
	Bent shaft
	FG6-11 opened to compensate.
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  

	Date
	Wash. Shore
	Bradford Is.

	3/20
	45.2
	45.4

	3/21
	45.5
	45.6

	3/22
	45.5
	45.6

	3/23
	45.5
	45.7

	3/24
	45.8
	46.1

	3/25
	46.2
	46.4

	3/26
	46.3
	46.4


4.4 Sensor Calibration.  Calibration was checked on 24 March.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 PH 1 Gantry Crane Delivery and Erection.  Construction continues.    

5.2 B2 VBS modifications.  Gatewell modifications are scheduled to begin in Winter 05/06.

5.3 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island fishway PLC are back in manual.  Electricians have determined the problems and are working on corrections.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft.  FG6-11 will be used to compensate until FG6-12 can be repaired.  FG6-12 will remain out of service until the fishway can be dewatered (2006/07).
6.1.3 A-branch diffusers have been reprogrammed to compensate for FG3-4 being out of service.  FG3-4 will remain out of service until the winter maintenance period 2005/06.
6.1.4 The AFF remains dewatered.  
6.2 Juvenile Fishways.  

6.2.1 DSM 1 will remain dewatered until 15 September.

6.2.2 SMF booster pump may be on order.

6.2.3 DSM2 mechanical screens were operated on 22 March.

7.  HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.
8.1 Marine mammals have been observed in the tailrace, the forebay, and the fishways.  The project is not taking action to harass, harm, or otherwise annoy these animals.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

