CENWP-OP-B                                                                                                                                  15 May 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 20 of 2005, which covers the period from 08 through 14 May 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 220.4 to 282.3 kcfs.  Daily average project tailwater elevation ranged from 18.3’ to 21.9’ msl.  Daily average powerhouse forebay elevation ranged from 74.1’ to 75.3’ msl.  Daily average river temperature ranged from 56 to 57(F.  Secchi disk measurements ranged from 3.5 to 5.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 73.1 to 91.9 kcfs.   

1.3 Unit operation.  

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.     

1.3.3 Unit 10 remains out of service for gantry crane three construction.

1.3.4 Unit 11 was out of service from 0658 until 1112 on 10 May for transducer repair.

1.3.5 Unit 13 was out of service form 0946 until 1312 on 09 May for transducer repair.

1.3.6 Unit 15 was out of service from 1315 until 1420 on 09 May for transducer repair.   Unit 15 was also out of service from 2251 until 2322 on 12 May due to a loss of power while shutting down Unit 16.

1.3.7 Unit 16 went out of service at 2251 on 12 May due to a breaker pole failure.  

1.3.8 Unit 17 was out of service from 2251 until 2324 on 12 May due to Unit 16 loss of power.

1.3.9 Unit 18 was out of service from 2251 until 2321 on 12 May due to Unit 16 loss of power.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week.  

2.1.1 FV4-3 and FV4-4 closed for cleaning from 0710 until 1006 on 09 May.

2.2 STS/VBS Inspections.   No STS/VBSs were inspected this reporting week.  

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 Battelle FPE and FGE.  The DIDSON camera is scheduled for installation on 18 May at PH1.

3.2 CRITFC.  Sampling continues twice a week through the summer.

3.3 ERDC TDG.  Sensors remain installed in the tailrace.

3.4 Fisheries Field Unit.  Monitoring and hazing of marine mammals entering the fishways.  See. 8.1
3.5 NOAA barge transportation study.  Barge arrival dates are tentatively scheduled for 30 April, 04, 14, and 20 May between 1930 and 0200 hours.  Tagged fish releases will occur 48 hours later.

3.6 ODFW Pikeminnow Tagging.  Electrofishing in Bonneville’s forebay and tailrace continued 09-13 May.
3.7 PSMFC.   Observed fallbacks included: 14 steelhead, one salmon and one unknown salmonid.  Research fish collected included: 333 clipped yearling chinook and 25 coho for NMFS, 570 clipped yearling chinook and 540 clipped steelhead for USGS. 
3.8 Spring Creek NFH.  Released approximately 340,000 tule fall chinook on 12 May.  
3.9 Univ of Idaho.  UI researchers are assisting with the marine mammal hazing.   Trapping continues. 

3.10 USDA Wildlife Services.   Hazing activities for gulls and sea lions continue.

3.11 USGS FPE and Survival.  Juvenile tracking continues.  
3.12 WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island. 

4.  FISHWAYS

4.1 Project biologists inspected 08 through 14 May.   

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper installation
	No action taken until winter maintenance.
	

	All week
	Cascades Is.
	FG6-12 OOS
	Bent shaft
	See 6.1.2
	

	All week
	AFF pickets
	#1 not fully raised
	Unknown
	TR submitted
	05-25112

	5/8
	B-branch
	FG 3-24 closed
	In manual
	Operators corrected
	

	5/8
	B-branch
	N. Entrance open
	In manual
	Operators corrected
	

	5/9
	B-branch
	FV4-3 and 4-4 closed, low diff.
	FV4-3 and 4-4 closed for cleaning
	Back in criteria by 1006
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  

	Date
	Wash. Shore
	Bradford Is.

	5/08
	56.5
	56.5

	5/09
	56.5
	56.6

	5/10
	56.3
	56.4

	5/11
	56.8
	56.7

	5/12
	57.0
	57.1

	5/13
	57.4
	57.5

	5/14
	57.5
	57.7











  Table 3.  Bonneville Fishway temperatures.

4.4 Sensor Calibration.  Calibration was checked on 13 May. 

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

5.2 B2 VBS modifications.  Gatewell modifications are scheduled to begin in winter 05/06.

5.3 Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

5.4 PH 1 Gantry Crane Delivery and Erection.  Crane testing performed this reporting week.

5.5 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

5.6 SMF Full flow PIT Tag Detectors.  A site visit, for location planning, is scheduled for 17 May.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island fishway PLCs are in manual.  
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and will remain out of service until winter 2006/07.  FG6-11 is used to compensate.
6.1.3 A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.
6.1.4 FV1-1 returned to auto at 0946 on 09 May.
6.2 Juvenile Fishways.  

6.2.1 SMF booster pump installation complete.

6.2.2 SMF switched to high outfall at 1545 on 09 May.

6.2.3 DSM2 mechanical screen sweeps operated at 1925 on 12 May.

7.  HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.
8.1 Marine mammals have been observed in the tailrace, forebay, and fishways.   FFU and UI are undertaking hazing activities; hydrophones are in the Washington Shore fishway entrance; sea lion exclusion devices are being designed for the fishway entrances.  

8.2 A teletype issued on 12 May revises the 120% gas cap to 125 kcfs.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

