CENWP-OP-B                                                                                                                                  22 May 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 21 of 2005, which covers the period from 15 through 21 May 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 241.9 to 290.8 kcfs.  Daily average project tailwater elevation ranged from 19.6’ to 22.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.3’ to 74.9’ msl.  Daily average river temperature was 58(F.  Secchi disk measurements ranged from 3.5 to 5.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 85.0 to 90.9 kcfs.   

1.3 Unit operation.   There was a continual 1% violation on 19 May.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.     

1.3.3 Unit 10 remains out of service for gantry crane three construction.

1.3.4 Unit 15 was out of service from 0657 on 20 May until 1225 on 21 May due to a STS failure.

1.3.5 Unit 16 returned to service at 1611 on 16 May.  

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week.  

2.1.1 FV1-1 closed for cleaning from 1555 until 1606 on 19 May.

2.1.2 FV3-7 closed for cleaning from 1329 until 1412 on 16 May.

2.1.3 FV6-7 closed for cleaning from 1515 until 1520 on 19 May.

2.2 STS/VBS Inspections.   No STS/VBSs were inspected this reporting week.  

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 Battelle FPE and FGE.  The DIDSON camera is scheduled for installation on 18 and 19 May at PH1.

3.2 CRITFC.  Sampling continues twice a week through the summer.

3.3 ERDC TDG.  Sensors remain installed in the tailrace.

3.4 Fisheries Field Unit (FFU).  Monitoring of marine mammals entering the fishways.  See. 8.1
3.5 ODFW/WDFW/NMFS.  Sea lion hazing resumed on 17 and 18 May.  See 8.2
3.6 NOAA barge transportation study.  Barge arrival dates are tentatively scheduled for 30 April, 04, 14, and 20 May between 1930 and 0200 hours.  Tagged fish releases will occur 48 hours later.

3.7 PSMFC.   Observed fallbacks: 10 steelhead, one salmon.  Fish for research included: 40 clipped yearling chinook and 25 coho for NMFS, 570 clipped yearling chinook and 570 clipped steelhead for USGS
3.8 Univ of Idaho.  Assisting with the marine mammal monitoring and observing.   Trapping in the AFF. 

3.9 USDA Wildlife Services.   Hazing activities for gulls and sea lions continue.

3.10 USGS FPE and Survival.  Juvenile tracking continues.  
3.11 USGS.  Assisting with marine mammal monitoring and observing.
3.12 WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island. 

4.  FISHWAYS

4.1 Project biologists inspected 15 through 21 May.   NOAA Fisheries inspected on 18 May.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper installation
	No action taken until winter maintenance.
	

	All week
	Cascades Is.
	FG6-12 OOS
	Bent shaft
	See 6.1.2
	

	5/15-17, 5/19, 5/21
	BI, A/B Branches
	Reading <1.3’
	Not in shad passage
	TR submitted
	#05-25787

	5/15, 5/17-21
	Cascades Is.
	UMT reading <1.3’
	Not in shad passage
	TR submitted
	#05-25786

	5/15, 5/17-19
	Weir 37/38
	Reading <1.3’
	Not in shad passage
	TR submitted
	#05-25778

	5/18
	PHI ITS
	Chaingate 3 closed
	DIDSON camera installation
	
	

	5/19
	B-Branch 
	FG3-22 closed
	Computer in manual
	Operators opened.
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  

	Date
	Wash. Shore
	Bradford Is.

	5/15
	57.7
	57.7

	5/16
	57.6
	57.6

	5/17
	57.8
	57.8

	5/18
	57.9
	58.0

	5/19
	57.9
	58.0

	5/20
	58.0
	58.0

	5/21
	57.8
	57.9











  Table 3.  Bonneville Fishway temperatures.

4.4 Sensor Calibration.  Calibration was checked on 21 May. 

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

5.2 B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

5.3 B2 VBS modifications.  Gatewell modifications are scheduled to begin in winter 05/06.

5.4 Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

5.5 PH 1 Gantry Crane Delivery and Erection.  Crane testing continues this reporting week.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

5.7 SMF Full flow PIT Tag Detectors.  CH2M Hill has been contracted to write the letter report.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island fishway PLCs are in manual.  
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and will remain out of service until winter 2006/07.  FG6-11 is used to compensate.
6.1.3 A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.
6.2 Juvenile Fishways.  

6.2.1 Chaingate 3C was closed from 1120 until 1620 on 18 May and from 0755 until 1200 on 19 May to facilitate the DIDSON camera installation.

6.2.2 SMF remains in the high outfall.

7.  HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.
8.1 Marine mammals have been observed in the tailrace, forebay, and fishways.   FFU, UI, and USGS continue monitoring.  Hydrophones are in the Washington Shore fishway entrance and sea lion exclusion devices are being built for the fishway entrances.  

8.2 Sea lion control devices were deployed from the powerhouse tailrace decks, corner collector and shorelines on 17 and 18 May.  After California seal control devices were used near the PH1 ice and trash sluiceway, approximately 300 juvenile salmonids were seen at the surface before disappearing from sight.  Several shad were also seen flopping on the surface after control devices were dropped.

8.3 A teletype issued on 19 May revises the 120% gas cap to 115 kcfs.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

