CENWP-OP-B                                                                                                                                  12 June 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 24 of 2005, which covers the period from 05 through 11 June 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 183.1 to 208.5 kcfs.  Daily average project tailwater elevation ranged from 15.8’ to 17.2’ msl.  Daily average powerhouse forebay elevation ranged from 73.9’ to 75.2’ msl.  Daily average river temperature ranged from 60 to 62(F.  Secchi disk measurements ranged from 5.0 to 6.5 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 88.7 to 98.6 kcfs.   

1.3 Unit operation.   

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.  

1.3.3 Unit 10 remains out of service for gantry crane three construction.

1.3.4 Unit 12 was out of service from 0700 until 0852 on 09 June for transducer repair.

1.3.5 Unit 17 was out of service from 0707 until 1109 on 07 June for transducer installation on trashrack.

1.3.6 Unit 18 was out of service from 1120 until 1642 on 07 June for transducer installation on trashrack.  Out of service from 0858 until 1144 on 09 June for transducer repair.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.
1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week.  

2.1.1 FV3-9 closed for cleaning from 0850 until 0855 on 06 June.

2.1.2 FV5-9 closed for cleaning from 1520 until 1525 on 09 June.

2.2 STS/VBS Inspections.   No STSs/VBSs were inspected this reporting week.  

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 Battelle FPE and FGE.  Monitoring continues.

3.2 CRITFC.  Sampling continues twice a week through the summer.

3.3 ERDC TDG.  Sensors remain installed in the tailrace.

3.4 NOAA Fish Lamprey.  The Bradford Island LPS in operation.

3.5 PSMFC.   Observed fallbacks: Four steelhead.  Research fish: 138 clipped steelhead for USGS.  Spring research concluded on 05 June.  Collections will resume next week with subyearling chinook.
3.6 Univ of Idaho.  Trapping in the AFF.  See 6.1.5 for SLED install/removal.
3.7 USDA Wildlife Services.   Hazing activities for gulls continue.

3.8 USGS FPE and Survival.  Juvenile tracking continues.  
3.9  WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island. 

4.  FISHWAYS

4.1 Project biologists inspected 05 June through 11 June.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Repairs scheduled for 06/07
	

	All week
	Cascades Is.
	FG6-12 OOS
	Bent shaft
	See 6.1.2
	

	6/5
	SA-24 Board 
	SUE bad indication
	Loose resistor 
	Repaired
	

	6/5, 6/10-11
	Weir 37
	Reading >1.3’
	Shad stuck on drain.
	Operators cleaned screen.  
	

	6/9
	Bradford Is.
	Reading >1.3’
	Unknown
	Operators adjusted
	

	6/9
	A-Branch
	Reading >1.3’
	Unknown
	Operators adjusted
	

	6/9
	B-Branch
	Reading >1.3’
	Unknown
	Operators adjusted
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.   The AFF is measured inside the lab, at the fish return.  

	Date
	Wash. Shore

Average
	Bradford Is.

Average
	AFF exit max

	6/5
	60.2
	60.1
	60.1

	6/6
	60.3
	60.2
	60.2

	6/7
	60.5
	60.6
	60.4

	6/8
	60.7
	60.7
	60.6

	6/9
	61.4
	61.4
	61.3

	6/10
	61.6
	61.7
	61.8

	6/11
	61.4
	61.4
	61.4


Table 3.  Bonneville Fishway temperatures.

4.4 Sensor Calibration.  Calibration was checked on 11 June.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

5.2 B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

5.3 B2 VBS modifications.  Gatewell modifications are scheduled to begin in winter 05/06.

5.4 Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

5.5 PH 1 Gantry Crane Delivery and Erection.  Nothing new to report.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

5.7 SMF Full flow PIT Tag Detectors.  CH2M Hill has been contracted to write the letter report.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island fishway PLCs are in manual.  Parts on order.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and will remain out of service until winter 2006/07.  FG6-11 is used to compensate.
6.1.3 A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.
6.1.4 PH1 NCCH sensor still OOS.  Channel elevation is now controlled from CCCH.
6.1.5 SLEDS were installed at all four PH2 entrances at 2041on 08 June.  SLEDS were removed from all entrances at 1948 on 10 June. 
6.2 Juvenile Fishways. 
6.2.1 The lower switchgate switched to the low outfall automatically at 15.8’ msl.

6.2.2 The hydrocannons were out of service for several hours on 08 June for line joint repairs.

7.  HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.
8.1 One marine mammal was observed by FFU on 10 June in the Bonneville tailrace this reporting week.   Hydrophones were removed from the Washington Shore fishway entrance.  

8.2 A teletype issued on 09 June revises the 120% gas cap to 140 kcfs.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

