CENWP-OP-B                                                                                                                                  26 June 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 26 of 2005, which covers the period from 19 through 25 June 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 155.2 to 224.8 kcfs.  Daily average project tailwater elevation ranged from 14.3’ to 18.3’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 75.2’ msl.  Daily average river temperature ranged from 62 to 65(F.  Secchi disk measurements ranged from 5.0 to 7.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 86.3 to 93.1 kcfs.   

1.3 Unit operation.   

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.  

1.3.3 Unit 3 was out of service from 0405 on 20 June until 1137 on 23 June for transformer maintenance.

1.3.4 Unit 4 was out of service from 0405 on 20 June until 1137 on 23 June for transformer maintenance.

1.3.5 Unit 10 remains out of service for gantry crane three construction.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.
1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week.  

2.1.1 FV3-9 closed for cleaning from 0718 until 0745 on 20 June.

2.1.2 FV5-9 closed for cleaning from 0815 until 0825 on 20 June.

2.1.3 FV6-9 closed for cleaning from 0745 until 0800 on 20 June and from 1345 until 1400 on 23 June.

2.2 STS/VBS Inspections.   No STSs/VBSs were inspected this reporting week.  

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.  
3.  RESEARCH
3.1 Battelle FPE and FGE.  Monitoring continues.

3.2 CRITFC.  Sampling continues twice a week through the summer.

3.3 CTUIR.  Collecting adult lamprey for re-establishment in the Umatilla River Basin. 

3.4 ERDC TDG.  Sensors remain installed in the tailrace.

3.5 NOAA Fish Lamprey.   The NDE ramp installation began on 22 June.  See 6.1.6
3.6 PSMFC.   Zero fallbacks were observed crossing the separator bars this week.  Subyearling chinook research fish collection: 1070 for USGS and 312 for NMFS.  
3.7 Univ of Idaho.  Trapping in the AFF.  See 6.1.5 for SLED install/removal.
3.8 USDA Wildlife Services.   Hazing activities for gulls continue.

3.9 USGS FPE and Survival.  Juvenile tracking continues.  
3.10  WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island. 

4.  FISHWAYS

4.1 Project biologists inspected 19 June through 25 June.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Repairs scheduled for 06/07
	

	All week
	Cascades Is.
	FG6-12 OOS
	Bent shaft
	See 6.1.2
	

	6/19, 6/21, 6/25
	Weir 37
	Reading >1.3’
	Shad stuck on drain.
	Operators notified/riggers cleaned screen
	

	6/23
	PH2 NDE
	Closed 
	Lamprey ramp installation.
	See 6.1.6
	

	6/25
	DSM2
	12A-S closed.
	Orifice inoperable for unknown reasons.
	Operators submitted TR
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.   The AFF is measured inside the lab at the fish return.  

	Date
	Wash. Shore

Average
	Bradford Is.

Average
	AFF exit max

	6/19
	63.2
	63.3
	63.4

	6/20
	63.9
	63.9
	64.0

	6/21
	64.3
	64.4
	64.4

	6/22
	64.3
	64.3
	64.4

	6/23
	64.6
	64.6
	64.6

	6/24
	64.5
	64.8
	64.6

	6/25
	64.6
	64.6
	64.5


Table 3.  Bonneville Fishway temperatures.

4.4 Sensor Calibration.  Calibration was checked on 25 June.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

5.2 B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

5.3 B2 VBS modifications.  Gatewell modifications are scheduled to begin in winter 05/06.

5.4 Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

5.5 PH 1 Gantry Crane Delivery and Erection.  Nothing new to report.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

5.7 SMF Full flow PIT Tag Detectors.  CH2M Hill has been contracted to write the letter report.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island fishway PLCs are in manual.  Parts on order.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and will remain out of service until winter 2006/07.  FG6-11 is used to compensate.
6.1.3 A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.
6.1.4 PH1 NCCH sensor still OOS.  Channel elevation is now controlled from CCCH.
6.1.5 SLEDS were installed at all four PH2 entrances at 2000 on 20 June.  SLEDS were removed from all entrances at 2000 on 22 June.   They will remain in the out position until further notice due to structural damage.  
6.1.6 Fish Unit discharge was lowered and the NDE gate closed at PH2 to reduce flow for installation of the lamprey ramp from 2000 until 2030 on 23 June.  The ramp is currently out of the water.  

6.2 Juvenile Fishways. 
7.  HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.
8.1 A new teletype was issued on 23 June raising the gas cap to 140 kcfs.   

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

