CENWP-OP-B                                                                                                                                  02 October 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 40 of 2005, which covers the period from 25 September through 01 October 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 77.4 to 114.7 kcfs.  Daily average project tailwater elevation ranged from 7.5’ to 10.7’ msl.  Daily average powerhouse forebay elevation ranged from 75.9’ to 76.2’ msl.  Daily average river temperature was 65(F.  Secchi disk measurements averaged ranged from 5.0 to 7.0 feet.

1.2 Daily average spill ranged from 1.3 to 1.4 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 6” during daylight hours.  

1.3 Unit operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab. 

1.3.3 Unit 6 remains out of service for a five-year overhaul.  

1.3.4 Unit 10 remains out of service for gantry crane three construction.

1.3.5 Unit 11 remains out of service due to a possible rotor failure.

1.3.6 Unit 12 operated outside the 1% band on 27 September due to STS inspections.  Unit 12 was out of service from 0655 until 0810 on 29 September for STS repair.

1.3.7 Unit 13 operated outside the 1% band on 27 September due to STS inspections.

1.3.8 Unit 14 operated outside the 1% band on 28 September due to STS inspections.

1.3.9 Unit 15 operated outside the 1% band on 28 September due to STS inspections.

1.3.10 Unit 16 operated outside the 1% band on 28 September due to STS inspections.

1.3.11 Unit 17 remains out of service for main unit circuit breaker replacement and T-12 switching.

1.3.12 Unit 18 remains out of service for main unit circuit breaker replacement and T-12 switching.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.
2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week

2.1.1 FV3-7 and FV3-9 were closed from 1010 until 1534 on 26 September due to discharged exhaust from the Spirit of Alaska at the Bradford Island boat dock.  Please see 7.1
2.1.2 FV3-7- closed from 1634 until 1650 on 27 September for cleaning.

2.1.3 FV3-9- closed from 1634 until 1650 on 27 September for cleaning.

2.2 STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.  

	Unit
	Date
	Run Hours
	Comments

	11
	9/27
	72
	Currently OOS

	12
	9/27
	690
	B slot screen repaired

	13
	9/27
	618
	

	14
	9/28
	657
	

	15
	9/28
	223
	

	16
	9/28
	241
	

	17
	9/28
	447
	Currently OOS.  VBS cleaned

	18
	9/28
	491
	Currently OOS


Table 1.  STS/VBS Inspections.
2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week. 
3.  RESEARCH
3.1 CRITFC.  Sampling two days a week continues.  

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA Fish Lamprey.  The BI exit PIT tag detector was removed from the exit gate slot on 26 September.  Washington Shore and BI ramps were taken out of service on 27 September.  

3.4 NOAA Fish PIT tag.  Tagging started the week of 26 September.

3.5 PSMFC.  Four fallback salmon were observed crossing the separator bars this week.  
3.6 Univ of Idaho.  Trapping and tagging continues.
3.7 WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.   

3.8 WDFW and ODFW.  Tule counting at Washington Shore and Bradford Island continues.

4.  FISHWAYS

4.1 Project biologists inspected 25 September through 01 October.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Will repair in 06/07
	

	All week
	B-Branch 
	North gate closed
	Separated from shaft
	See 6.1.4
	

	9/25-26, 9/29-10/1
	Weir 37
	Reading <1.0>
	About .1’ out of criteria.  
	May be OCC due to AFF ops.  Operators informed.
	

	9/25-26, 9/28
	A-Branch 
	FG3-3 not controlling for TW.
	Diffuser in manual.  Cannot be adjusted.
	No action taken.  Repairs scheduled for Winter 05/06
	

	9/29
	Cascades Is
	North gate open
	System in manual
	Operators closed entrance gate
	

	9/29
	Cascades Is
	Entrance head low
	North gate open
	See above
	

	9/30
	Cascades Is
	FG6-14 closed 
	System in manual 
	Operators opened diffuser.
	

	9/30
	B-Branch
	FG3-27 closed
	System in manual
	Operators opened diffuser.
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  

	Date
	WA Shore Average
	Bradford Is Average

	9/25
	65.2
	65.1

	9/26
	65.1
	65.0

	9/27
	65.1
	65.0

	9/28
	65.2
	65.0

	9/29
	65.1
	65.0

	9/30
	65.1
	65.1

	10/1
	65.1
	64.9


Table 3.  Bonneville Fishway temperatures.

4.4 Sensor Calibration.  Calibration was checked on 29 September.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

5.2 B2 Fish Unit Trash rake.  Delivery and installation sometime before winter.

5.3 B2 VBS modifications.  Gatewell modifications to begin in Unit 13 starting early November.

5.4 Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

5.5 Main Unit Circuit Breaker.  Mods continue with Units 17/18.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.7 SMF Full flow PIT Tag Detectors.  No new updates.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  FG6-11 is used to compensate.
6.1.3 A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.
6.1.4 B-Branch north gate has separated from the shaft.  The south gate compensates when possible.  

6.1.5 FV3-7 and FV3-9 closed from 1010 until 1534 on 26 September due to Spirit of Alaska exhaust discharge in near the fishway.  Please see 7.1
6.1.6 The lamprey PIT tag detector was removed from the Bradford Island exit gate slot at 1458 on 26 September.  The leaf gates have been reinstalled and the exit is properly functional again.

6.2 Juvenile Fishways.
6.2.1 DSM2 screen sweeps are exercised on Sunday evenings.

6.2.2 DSM1 was closed from 1012 until 1548 on 26 September due to Spirit of Alaska exhaust discharge upstream of the fishway.  Please see 7.1
6.2.3 The PH1 ITS was closed from 1038 until 1456 on 26 September due to Spirit of Alaska exhaust discharge upstream of the fishway.  Please see 7.1
6.2.4 Chaingates 1C, 3C, and 6C were closed to accommodate construction activities on the +90’ deck from 1329 on 26 September until 0736 on 27 September.  Chaingates 7A, 7B, and 9B were used to compensate during that time.

6.3 Upcoming Events.
6.3.1 FPOM will be held at Bonneville Dam on 13 October.

6.3.2 The JMF will go to bypass at 0700 on 31 October.

6.3.3 The UMT is scheduled to go OOS (to accommodate VBS modification work) on 31 October.

6.3.4 Cascades Island is scheduled to open on 31 October.

7.  HAZMAT, SPILLS AND CLEANUP 
7.1 On 26 September, the Spirit of Alaska discharged exhaust at the boat dock on Bradford Island.  A Project Fisheries MFR, dated 28 September 2005, was sent to NOAA Fisheries, CRITFC, and FPC.  Requests for copies of the final Environmental Compliance Coordinator report should be directed to Bonneville Lock and Dam.
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.
8.1 A 27 September teletype requests Bonneville maintain a forebay of 75.0-76.5’ msl from 0600 on 28 September until 1800 on 30 September.  This is to limit wear and tear on tribal gillnet equipment.

8.2 Proposed FPP changes to Appendix G and the inclusion of a new appendix for the JMF are available from Project Fisheries.

8.3 The 2005/06 Winter Maintenance Schedule is available from Project Fisheries.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

