CENWP-OP-B                                                                                                                                  31 October 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 43 of 2005, which covers the period from 23 through 29 October 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 85.5 to 119.1 kcfs.  Daily average project tailwater elevation ranged from 8.5’ to 11.0’ msl.  Daily average powerhouse forebay elevation ranged from 74.1’ to 75.2’ msl.  Daily average river temperature ranged from 60 to 61(F.  Secchi disk measurements averaged 7.0 feet.

1.2 Daily average spill ranged from 1.1 to 1.2 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 6” during daylight hours.   

1.3 Unit operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab. 

1.3.3 Unit 6 remains out of service for a five-year overhaul.  

1.3.4 Unit 10 remains out of service for gantry crane three construction.

1.3.5 Unit 11 remains out of service due to a rotor failure.

1.3.6 Unit 12 remains out of service for MUCB replacement.

1.3.7 Unit 14 had a 1% violation on 26 October for STS inspection.

1.3.8 Unit 15 had a 1% violation on 26 October for STS inspection.

1.3.9 Unit 16 had a 1% violation on 26 October for STS inspection.

1.3.10 Unit 17 had a 1% violation on 26 October for STS inspection.

1.3.11 Unit 18 had a 1% violation on 26 October for STS inspection.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed this reporting week

2.2 STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.  

	Unit
	Date
	Run Hours
	Comments

	11
	10/26
	
	Out of service

	12
	10/26
	357
	

	13
	10/26
	
	No inspection.  Remove on 11/1/05

	14
	10/26
	676
	

	15
	10/26
	673
	

	16
	10/26
	607
	

	17
	10/26
	352
	VBSs need cleaned

	18
	10/26
	340
	


Table 1.  STS/VBS Inspections.
2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week. 
3.  RESEARCH
3.1 CRITFC.  Sampling concluded on 24 October.  

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 PSMFC.  One adult salmon was observed crossing the separator bars this week.  
3.4 WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.   

4.  FISHWAYS

4.1 Project biologists inspected 23-26, 27-29 October.  

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Will repair in 06/07
	

	All week
	B-Branch 
	North gate closed
	Separated from shaft
	See 6.1.4
	

	10/23
	Cascades Is.
	Differential high
	System in manual
	Operators adjusted FV5-4, FV5-3
	

	10/23-24
	B-Branch
	Differential high and low
	System in manual
	Operators adjusted FV4-4, FV4-3
	

	10/24-25
	B-Branch
	FG 3-27 position 
	System in manual
	
	

	10/25-26
	BI, A and B branch gauge
	Reading <1.0’
	Unknown
	
	

	10/27
	
	No inspection by fisheries
	Scheduling conflicts due to training
	
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  

	Date
	WA Shore Average
	Bradford Is Average

	10/23
	61.3
	61.0

	10/24
	61.5
	61.4

	10/25
	61.5
	61.3

	10/26
	61.2
	61.0

	10/27
	60.6
	60.5

	10/28
	60.2
	60.0

	10/29
	60.3
	60.0


Table 3.  Bonneville Fishway temperatures.

4.4 Sensor Calibration.  Calibration was checked on 29 October.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

5.2 B2 Fish Unit Trash rake.  Delivery and installation sometime before winter.

5.3 B2 VBS modifications.  Gatewell modifications to begin in Unit 13 starting early November.

5.4 Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

5.5 Main Unit Circuit Breaker.  Mods continue on Units 11/12.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.7 SMF Full flow PIT Tag Detectors.  Evaluating a fiberglass section of pipe.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  FG6-11 is used to compensate.
6.1.3 A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.
6.1.4 B-Branch north gate has separated from the shaft.  The south gate compensates when possible.  

6.2 Juvenile Fishways.
6.2.1 DSM2 screen sweeps are exercised on Sunday evenings.

6.3 Upcoming Events.
6.3.1 The JMF will go to bypass at 0700 on 31 October.

6.3.2 The UMT is scheduled to go OOS (to accommodate VBS modification work) on 31 October.

6.3.3 Cascades Island is scheduled to open on 31 October.

7.  HAZMAT, SPILLS AND CLEANUP.  Nothing to report
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.  Nothing to report
JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

