CENWP-OP-B                                                                                                                                  13 November 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 46 of 2005, which covers the period from 06 through 12 November 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 112.4 to 135.6 kcfs.  Daily average project tailwater elevation ranged from 11.1’ to 12.9’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 75.1’ msl.  Daily average river temperature ranged from 55 to 56(F.  Secchi disk measurements averaged 5.0 to 7.0 feet.

1.2 Daily average spill ranged from 0.7 to 1.2 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 6” during daylight hours.   

1.2.1 Spillbay 18 was on seal from 0800 until 1220 on 08 November to facilitate HSS inspections of the B-Branch transverse bulkheads.

1.2.2 Spillbay 1 was on seal from 1220 until 1605 to facilitate HSS inspections on the Cascades Island transverse bulkheads.

1.3 Unit operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab. 

1.3.3 Unit 6 remains out of service for a five-year overhaul.  

1.3.4 Unit 10 remains out of service for gantry crane three construction.

1.3.5 Unit 11 remains out of service due to a rotor failure.

1.3.6 Unit 13 remains out of service for VBS mods and a four-year overhaul.

1.3.7 Unit 14 remains out of service for MUCB replacement.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

1.4.1 Trashracks on F2 were raked from 1305 until 1315 on 08 November.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures. The following AWS valves were closed this reporting week

2.1.1 FV1-1 closed for cleaning from 0758 until 0815 on 07 November.

2.1.2 FV3-7 closed for cleaning from 0806 until 0845 on 09 November.

2.1.3 FV3-9 closed for cleaning from 0806 until 0845 on 09 November.

2.1.4 FV4-3/4-4 closed for HSS inspections from 0800 until 1220 on 08 November.

2.1.5 FV5-3/5-4 closed for HSS inspections from 1220 until 1605 on 08 November.

2.2 STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.  

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week. 
3.  RESEARCH
3.1 Battelle/Normandeau.  Sensor fish equipment tested in Unit 16 on 08-09 November.  Fish to be released after Thanksgiving.

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 WDFW Fish Counting.  16-hr video counting at Cascades Island, Washington Shore and Bradford Island.

4.  FISHWAYS

4.1 Project biologists inspected 06 through 12 November.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Will repair in 06/07
	

	All week
	B-Branch 
	North gate closed
	Separated from shaft
	See 6.1.4
	

	11/7, 11/11-12
	BI, A and B branch weirs
	Reading <1.0>
	Low Forebay
	No action taken.
	

	11/7, 11/9
	Weir 37
	Reading <1.0>
	Unknown
	Operators cleaned valve.
	

	11/7-12
	DSM2 
	Airburst OOS
	PLC failure
	TR sent to electricians.
	

	11/8
	B-Branch/ CI
	System shutdown
	HSS inspections
	See 6.1.6 and 6.1.7
	

	11/09-12
	PH1 ITS chain gates.
	3C closed.  1B opened. Adjacent gates not opened.
	Gross head sensing work.
	3A will be opened on 11/14.
	

	11/9
	B-Branch
	Proper diffusers not open.
	System in manual.
	Operators adjusted.
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  

	Date
	WA Shore Average
	Bradford Is Average

	11/06
	56.6
	56.5

	11/07
	56.3
	56.3

	11/08
	56.2
	56.0

	11/09
	55.5
	55.5

	11/10
	54.9
	54.9

	11/11
	55.0
	54.9

	11/12
	54.7
	54.6


Table 3.  Bonneville Fishway temperatures.

4.4 Sensor Calibration.  Calibration was checked on 11 November.  B-Branch and Cascades Island are out of calibration until sensors can be replaced and recalibrated.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Construction activities have begun.

5.2 B2 Fish Unit Trash rake.  Delivered on 31 October.  Modifications still needed.

5.3 B2 VBS modifications.  Gatewell VBS slot modifications continue on Unit 13.

5.4 Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

5.5 Main Unit Circuit Breaker.  Mods continue on Units 13/14.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.7 SMF Full flow PIT Tag Detectors.  Team meeting scheduled for 07 November.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  FG6-11 is used to compensate.
6.1.3 A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.
6.1.4 B-Branch north gate has separated from the shaft.  The south gate compensates when possible.  

6.1.5 Cascades Island fishway exit remains open.

6.1.6 On 08 November, B-Branch head was reduced to zero from 0800 until 1220.  This was to facilitate the pulling and HSS inspection of the transverse bulkheads between the fishway and Bay 18.  

6.1.7 On 08 November, Cascades Island head was reduced to zero from 1220 until 1605.  This was to facilitate the pulling and HSS inspection of the transverse bulkheads between the fishway and Bay 1.  

6.1.8 Bradford Island picket leads were cleaned on 09 November.

6.2 Juvenile Fishways.
6.2.1 The DSM2 airburst system went out of service at 1646 on 08 November.  It may be operated in manual.

6.2.2 DSM2 screen sweeps were operated in manual twice a day starting 09 November.  Debris loads require the system to be operated more often.  The screen sweeps were switched to auto on a six hour cycle at 0930 on 10 November.

6.2.3 Chain gate 3C was closed at 1150 on 08 November due to gross head sensing work.  1B was opened to compensate.  

6.3 Upcoming Events.
6.3.1 AFEP review at Walla Walla from 14-17 November.

6.3.2 Bradford Island dewatering on 05 December.

7.  HAZMAT, SPILLS AND CLEANUP.  Nothing to report
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.  
8.1 A teletype on 03 November requests a forebay between 73.0 to 74.0’ msl from 0800 until 1500 on 07 November.  This request was made by Skamania Co. Noxious Weed Board to facilitate inspection of Drano Lake for future milfoil control treatment.
8.2 A teletype on 04 November requests the following tailwater adjustments to occur on 09 November.  This request is so researchers can test the hydrophones to be used in the chum spawning studies later this month.
0800 HRS. HOLD TW AT 11.5 FEET

1000 HRS. INCREASE TW FROM 11.5 FT TO 13.5 FEET

1200 HRS. INCREASE TW FROM 13.5 FT TO 15.5 FEET

1400 HRS. DECREASE TW FROM 15.5 FT TO 11.5 FEET

8.2.1 The Project was unable to maintain a tailwater higher than 13.9’ to meet the teletype request.  

8.3 A teletype issued on 10 November requests hard tailwater constraint of 11.3’ to 11.7’ between 0700 and 1900 daily and no less than 11.3’ at any time.  This is to facilitate chum spawning around Ives and Pierce Islands.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

