CENWP-OP-B                                                                                                                                  27 November 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 48 of 2005, which covers the period from 20 through 26 November 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 121.4 to 137.9 kcfs.  Daily average project tailwater elevation ranged from 11.5’ to 12.8’ msl.  Daily average powerhouse forebay elevation ranged from 72.7’ to 74.1’ msl.  Daily average river temperature ranged from 49 to 51(F.  Secchi disk measurements averaged 4.0 to 7.0 feet.

1.2 Daily average spill ranged from 1.1 to 1.2 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 6” during daylight hours.   

1.3 Unit operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 1 was out of service from 1007 until 1138 on 23 November for STS repair.

1.3.3 Unit 2 remains out of service for turbine rehab. 

1.3.4 Unit 6 returned to service at 1514 on 21 November.  

1.3.5 Unit 10 remains out of service for turbine rehab.

1.3.6 Unit 11 remains out of service due to a rotor failure.

1.3.7 Unit 13 remains out of service for VBS mods and a four-year overhaul.

1.3.8 Unit 14 remains out of service for MUCB replacement.

1.3.9 Unit 17 was out of service from 1030 until 1154 on 20 November and from 1044 until 1126 on 22 November for VBS cleaning.

1.3.10 Unit 18 operated outside the 1% from 1255 until 1515 on 25 November to facilitate trashrack raking.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 1800-0500 nightly due to milfoil and excessive drawdowns.

1.4.1 The following times and dates are when F1 was at reduced load or out of service.

1.4.1.1 20 November- returned to service at 1653

1.4.1.2 21 November- reduced load for raking from 1159 until 1628.

1.4.1.3 22 November- out of service at 1201 due to breaker failure.

1.4.1.4 23 November- returned to service at 1352, reduced load for floating at 1720.

1.4.1.5 25 November- reduced load for raking from 1035 until 1230.

1.4.2 The following times and dates are when F2 was at reduced load or out of service.

1.4.2.1 20 November- returned to service at 1658.

1.4.2.2 21 November- reduced load for raking from 1159 until 1631.

1.4.2.3 22 November- out of service for raking from 1201 until 1637.

1.4.2.4 23 November- reduced load for raking from 1355 until 1652, reduced load for floating at 1720.

1.4.2.5 25 November- reduced load for raking from 1008 until 1230.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures. The following AWS valve activities occurred this reporting week.

2.1.1 FV1-1 

2.1.1.1 20 November- closed from 0730 until 0825 for cleaning.

2.1.1.2 21 November- closed from 0818 until 0859 for cleaning, closed at 1839 to float trash.

2.1.1.3 22 November- opened at 0525, closed from 0705 until 0751 for cleaning, closed at 2338 to float trash. 

2.1.1.4 23 November- opened at 0515, closed from 1145 until 1200 for cleaning, closed at 1725 to float trash.

2.1.1.5 24 November- opened at 0520, closed at 1756 to float trash.

2.1.1.6 25 November- opened at 0515, closed from 0820 until 0850 for cleaning, closed at 1700 to float trash.

2.1.1.7 26 November- opened at 0712, closed for cleaning from 1424 until 1448.

2.1.2 FV3-7

2.1.2.1 21 November- closed for cleaning from 1015 until 1051.

2.1.2.2 22 November- closed for cleaning from 0805 until 0830.

2.1.2.3 26 November- closed for cleaning from 1311 until 1400.

2.1.3 FV3-9

2.1.3.1 20 November- closed for cleaning from 0650 until 0725.

2.1.3.2 21 November- closed for cleaning from 0958 until 1051.

2.1.3.3 22 November- closed for cleaning from 0805 until 0830.

2.1.3.4 25 November- closed for cleaning from 0845 until 0915.

2.1.3.5 26 November- closed for cleaning from 1350 until 1415.

2.1.4 Cascades Island exit was throttled for cleaning from 1000 until 1030 on 25 November.

2.1.5 FV5-9 was closed for cleaning from 1000 until 1030 on 25 November.

2.2 STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.  

	Unit
	Date
	Run Hours
	Comments

	1
	11/23
	815
	Cord repair/ rivet replacement

	3
	11/23
	842
	


Table 1.  STS/VBS Inspections.
2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week. 
3.  RESEARCH
3.1 Battelle/Normandeau.  Sensor fish to be released after Thanksgiving.

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 WDFW Chum.  Trapping and tagging continues.

3.4 WDFW Fish Counting.  16-hr video counting at Cascades Island, Washington Shore and Bradford Island.

4.  FISHWAYS

4.1 Project biologists inspected 20 through 26 November.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Will repair in 06/07
	

	All week
	B-Branch 
	North gate closed
	Separated from shaft
	See 6.1.4
	

	All Week
	DSM2 
	Airburst OOS
	PLC failure
	TR sent to electricians.
	06-8326

	All week
	Trashracks
	High head diff.
	Milfoil 
	Cleaned almost daily.
	

	11/20, 11/22-26
	BI, A and B branch weirs
	Reading <1.0>
	Low Forebay, trashrack differential
	No action taken.
	

	11/20-26
	Weir 37
	Reading <1.0>.
	Unknown
	Riggers cleaned valve.
	

	11/20, 11/22
	Fish Units
	OOS
	Raking trashracks
	Following FPP criteria
	

	11/20, 11/22
	WS monoliths
	Differential <1.5’
	Fish Units OOS
	Following FPP criteria
	

	11/21
	Weir 38
	Reading <1.0>
	Unknown
	
	

	11/22-23
	PH1 PCC
	Differential <1.5’
	FV1-1 trashrack
	Riggers cleaned valve.
	

	11/23
	DSM2
	ERG tripped
	Possibly due to high debris loads.
	Screen cleaners set to run every hour.
	

	11/26
	CI diffusers
	FG6-13, 6-12 
	System in manual
	Operators opened diffusers.
	

	11/26
	B-Branch diff
	FG3-26, 3-25
	System in manual
	Operators opened diffusers.
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  

	Date
	WA Shore Average
	Bradford Is Average

	11/20
	50.9
	50.8

	11/21
	50.5
	50.4

	11/22
	49.9
	49.9

	11/23
	49.6
	49.6

	11/24
	49.1
	49.1

	11/25
	49.1
	49.2

	11/26
	49.5
	49.5


Table 3.  Bonneville Fishway temperatures.

4.4 Sensor Calibration.  Calibration was checked on 23 November.  B-Branch and Cascades Island are out of calibration until sensors can be replaced and recalibrated.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Demolition and construction continue.

5.2 B2 Fish Unit Trash rake.  Modifications complete.

5.3 B2 VBS modifications.  Gatewell VBS slot modifications continue on Unit 13.

5.4 Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

5.5 Main Unit Circuit Breaker.  Mods continue on Units 13/14.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.7 SMF Full flow PIT Tag Detectors.  No new updates.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.
6.1.3 B-Branch north gate has separated from the shaft.  The south gate compensates when possible.  

6.1.4 Washington Shore monoliths returned to FPP criteria at 1655 on 20 November.  

6.1.5 Washington Shore monoliths were set for one Fish Unit configuration from 1640 on 22 November until 1652 on 23 November.

6.1.6 During the week of 20-26 November, the Project experienced increased milfoil debris in the trashracks of AWS valves, VBSs and Fish Unit trashracks.  Riggers were called in throughout the holiday weekend to keep trashracks clean.  

6.2 Juvenile Fishways.
6.2.1 The DSM2 airburst system remains out of service, though it may be operated in manual.

6.2.2 Gatewell orifices were often closed while raking trashracks and cleaning VBSs.  The mechanical screen cleaners were put into continuous mode during cleaning.  The following is the orifices and times of closure.

6.2.2.1 Unit 17 from 1030 until 1154 on 20 November.

6.2.2.2 F2 A-S and B-S from 1240 until 1611 on 21 November.

6.2.2.3 F1 A-N and B-N from 1317 until 1615 on 21 November.

6.2.2.4 Unit 17 A-N from 1053 until 1129; B-N from 1128 until 1148; C-N from 1318 until 1340 on 22 November.

6.2.2.5 F2 A-S and B-S from 1500 until 1532 on 22 November.

6.2.2.6 F1 A-N and B-N from 1532 until 1555 on 22 November.

6.2.3 DSM2 screen cleaners in auto.  As of 22 November, the screen cleaners are on one hour cycles. 

6.2.4 DSM2 ERG tripped at 1700 on 23 November.  No cause has been found.  The system was restored to normal condition by 1755 on 23 November.

6.3 Upcoming Events.
6.3.1 Bradford Island dewatering on 05 December.

7.  HAZMAT, SPILLS AND CLEANUP.  Nothing to report
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.  
8.1 A teletype issued on 10 November requests hard tailwater constraint of 11.3’ to 11.7’ between 0700 and 1900 daily and no less than 11.3’ at any time.  This is to facilitate chum spawning around Ives and Pierce Islands.

8.2 A teletype issued on 18 November, requesting TW elevations for 21 November was cancelled.

8.3 A teletype issued on 23 November requests the following tailwater adjustments to occur on 26 November.  This request is for chum spawning studies.  The objective is to achieve desired tailwater as quickly and smoothly as possible and to hold that elevation for the time requested.  The study is looking at how flow velocity affects chum spawning behaviour.  Once 11.5’ msl is reached, return to guidance per TTY RCC R 111005 1546 CO, Tailwater operation for chum spawning (see 8.1).  If target TW elevations cannot be reached, the Project is to hold TW as high as possible.
8.3.1 26 November tailwater elevations are as follows
8.3.1.1 0600 increase from 11.5’ to 13.5’

8.3.1.2 0700 increase from 13.5’ to 15.5’

8.3.1.3 1500 decrease from 15.5’ to 13.5’

8.3.1.4 1600 decrease from 13.5’ to 11.5’

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

