CENWP-OP-B                                                                                                                                  05 December 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 49 of 2005, which covers the period from 27 November through 03 December 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 107.5 to 135.4 kcfs.  Daily average project tailwater elevation ranged from 11.4’ to 13.0’ msl.  Daily average powerhouse forebay elevation ranged from 73.7’ to 75.2’ msl.  Daily average river temperature ranged from 47 to 49(F.  Secchi disk measurements averaged 5.5 to 7.0 feet.

1.2 Daily average spill ranged from 0.5 to 1.1 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 6” during daylight hours.  Spill bay 18 was not reopened on 01 December, when B-Branch went to orifice flow.  Spill bay 1 remains open 6” during daylight hours to provide attraction flow for Cascades Island.

1.3 Unit operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab. 

1.3.3 Unit 10 remains out of service for turbine rehab.

1.3.4 Unit 11 remains out of service due to a rotor failure.

1.3.5 Unit 12 operated outside the 1% from 0740 until 0805 on 28 November to facilitate STS inspections and was out of service from 1238 until 1533 on 30 November for STS repairs.

1.3.6 Unit 13 remains out of service for VBS mods and a four-year overhaul.

1.3.7 Unit 14 remains out of service for MUCB replacement.

1.3.8 Unit 16 was raked from 1049 until 1316 on 27 November; operated outside the 1% from 0955 until 1106 to facilitate STS inspections and was out of service from 1341 until 1630 for STS repairs on 28 November.

1.3.9 Unit 17 was raked from 0903 until 1043 on 27 November and operated outside the 1% from 1106 until 1202 on 28 November to facilitate STS inspections.

1.3.10 Unit 18 was raked from 0808 until 0853 on 27 November; operated outside the 1% from 1241 until 1341 on 28 November to facilitate STS inspections; and was out of service from 1059 until 1553 on 29 November and from 0757 until 0930 on 30 November for STS repairs.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 1800-0500 nightly due to milfoil and excessive drawdowns.

1.4.1 F1 was at reduced load for trashrack raking from 0800 until 0906, from 0942 until 1100 and from 1259 until 1436 on 27 November.

1.4.2 F2 was at reduced load for trashrack raking from 0800 until 1043, from 0942 until 1100, and from 1259 until 1436 on 27 November.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures. The following AWS valve activities occurred this reporting week.

2.1.1 FV1-1- closed to float trash from 2102 on 27 November until 0500 on 28 November, and closed at 0020 on 01 December due to Bradford Island going to orifice flow.

2.1.2 FV3-7- closed for cleaning from 1457 until 1505 on 27 November and closed at 0020 on 01 December due to Bradford Island going to orifice flow.

2.1.3 FV3-9- closed for cleaning from 1457 until 1505 on 27 November and closed at 0020 on 01 December due to Bradford Island going to orifice flow.

2.1.4 FV4-3/4-4- closed at 0130 on 01 December due to Bradford Island going to orifice flow.

2.1.5 FV5-9 was closed for cleaning from 1350 until 1400 on 27 November.

2.1.6 The FERL intake was cleaned at 1635 on 29 November.

2.2 STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.  

	Unit
	Date
	Run Hours
	Comments

	11
	
	
	OOS

	12
	11/28
	577
	Repaired rips and popped rivets in A-slot

	13
	
	127
	STSs removed on 11/01

	14
	11/28
	167
	OOS

	15
	11/28
	770
	

	16
	11/28
	765
	Repaired rips in A-slot.  B-slot had 25% of mesh missing.

	17
	11/28
	741
	VBSs had high aquatic vegetation loads

	18
	11/28
	765
	Replaced A-slot and B-slot, repaired rips in C-slot


Table 1.  STS/VBS Inspections.
2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week. 
3.  RESEARCH
3.1 Battelle/Normandeau.  Sensor fish postponed until further notice.

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 WDFW Chum.  Trapping and tagging continues.

3.4 WDFW Fish Counting.  16-hr video counting at Cascades Island, Washington Shore and Bradford Island.

4.  FISHWAYS

4.1 Project biologists inspected 27 through 30 November and 02 December.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Will repair in 06/07
	

	All Week
	DSM2 
	Airburst OOS
	PLC failure
	TR sent to electricians.
	06-8326

	11/27-11/30
	B-Branch 
	North gate closed
	Separated from shaft
	See 6.1.4
	

	11/27-11/30
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	11/27
	Trashracks
	High head diff.
	Aquatic vegetation
	Riggers cleaned throughout the week.
	

	11/27, 11/30, 12/2
	Weir 38
	Reading <1.0>
	Unknown
	
	

	11/27
	Fish Units
	OOS
	Raking trashracks
	Following FPP criteria
	

	11/27
	WS monoliths
	Differential <1.5’
	Fish Units OOS
	Following FPP criteria
	

	11/27
	B-Branch diff
	FG3-26, 3-25
	System in manual
	Operators opened diffusers.
	

	11/30, 12/2
	Weir 37
	Reading <1.0>
	Clogged trashrack
	Riggers cleaned trashrack.
	

	12/2
	Weir 67
	Reading <1.0>
	UMT OOS
	FV6-9 closed.
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  

	Date
	WA Shore Average
	Bradford Is Average

	11/27
	49.2
	49.3

	11/28
	48.6
	48.5

	11/29
	48.0
	47.9

	11/30
	47.8
	47.8


Table 3.  Bonneville Fishway temperatures.

4.4 Sensor Calibration.  Calibration was checked on 30 November.  B-Branch and Cascades Island are out of calibration until sensors can be replaced and recalibrated.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Demolition and construction continue.

5.2 B2 VBS modifications.  Gatewell VBS slot modifications continue on Unit 13.

5.3 Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

5.4 Main Unit Circuit Breaker.  Mods continue on Units 13/14.

5.5 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.6 SMF Full flow PIT Tag Detectors.  No new updates.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.
6.1.3 B-Branch north gate has separated from the shaft.  The south gate compensates when possible.  

6.1.4 The Project experienced increased milfoil debris in the trashracks of AWS valves, VBSs and Fish Unit trashracks.  Riggers were called in throughout the holiday weekend to keep trashracks clean.  

6.1.5 Bradford Island went to orifice flow at 0020 on 01 December.

6.2 Juvenile Fishways.
6.2.1 DSM2 screen cleaners in auto and on one hour cleaning cycles. 

6.2.2 DSM2 ERG trip that occurred on 23 November appears to have been caused by a combination of the cycling of the PLC and the increased aquatic debris.  The PLC cycling resulted in a power outage that left the PLC temporarily frozen.  During this time, the PLC was not able to regulate the DSM elevations.  At the same time, debris loads surpassed screen sweep capacity (set for 3 hour cycles).  When the ERG sensor reached the high water elevation, the ERG automatically tripped open.  The ERG is NOT controlled by the PLC but by a stillwell, independent of the PLC.   

6.3 Upcoming Events.
6.3.1 PH1 and PH2 STS removal on 15-16 December.

6.3.2 PH1 DSM dewatering on 19 December.

6.3.3 PH2 DSM dewatering on 20 December.

6.3.4 Two-mile pipe inspection on 20-21 December.

7.  HAZMAT, SPILLS AND CLEANUP.  Nothing to report
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.  
8.1 A teletype issued on 10 November requests hard tailwater constraint of 11.3’ to 11.7’ between 0700 and 1900 daily and no less than 11.3’ at any time.  This is to facilitate chum spawning around Ives and Pierce Islands.

8.2 A teletype issued on 30 November requests the following tailwater adjustments to occur on 30 November and 02 December.  This request is for chum spawning studies.  The objective is to achieve desired tailwater as quickly and smoothly as possible and to hold that elevation for the time requested.  The study is looking at how flow velocity affects chum spawning behaviour.  Once 11.5’ msl is reached, return to guidance per TTY RCC R 111005 1546 CO, Tailwater operation for chum spawning (see 8.1).  If target TW elevations cannot be reached, the Project is to hold TW as high as possible.
8.2.1 30 November tailwater elevations are as follows:
8.2.1.1 1600 increase from 11.5’ to 13.5’

8.2.1.2 1700 increase from 13.5’ to 15.5’

8.2.1.3 0100 decrease from 15.5’ to 13.5’

8.2.1.4 0200 decrease from 13.5’ to 11.5’

8.2.2 02-03 December tailwater elevations are as follows (revised with a teletype sent on 01 December):

8.2.2.1 1600 increase from 11.5’ to 13.5’

8.2.2.2 1700 increase from 13.5’ to 15.5’

8.2.2.3 0100 decrease from 15.5’ to 13.5’

8.2.2.4 0200 decrease from 13.5’ to 11.5’

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

