CENWP-OP-B                                                                                                                                  12 December 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 50 of 2005, which covers the period from 04 through 10 December 2005.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 117.9 to 144.1 kcfs.  Daily average project tailwater elevation ranged from 11.5’ to 13.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 75.3’ msl.  Daily average river temperature ranged from 44 to 47(F.  Secchi disk measurements averaged 7.0 feet.

1.2 Daily average spill was 0.5 kcfs.   Spill Bay 1, which supplies attraction flow for Cascades Island, is open 6” during daylight hours.  

1.3 Unit operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 1 had a 1% violation on 10 December due to reactivity testing.  

1.3.3 Unit 2 remains out of service for turbine rehab. 

1.3.4 Unit 3 had a 1% violation on 10 December due to reactivity testing.  

1.3.5 Unit 4 had a 1% violation on 10 December due to reactivity testing.

1.3.6 Unit 5 had a 1% violation on 10 December due to reactivity testing.  

1.3.7 Unit 10 remains out of service for turbine rehab.

1.3.8 Unit 11 remains out of service due to a rotor failure.

1.3.9 Unit 12 was out of service from 0410 until 1010 on 08 December for T11 outage.

1.3.10 Unit 13 remains out of service for VBS mods and a four-year overhaul.

1.3.11 Unit 14 returned to service at 1745 on 08 December.

1.3.12 Unit 17 had a 1% violation on 05 December due to VBS cleaning.  

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 1800-0500 nightly due to aquatic vegetation and excessive drawdowns.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed this reporting week.

2.2 STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.  

2.3 Dewatering and Fish Salvage.  The following dewatering and salvage activities occurred this reporting week. 
Bradford Is., A-Branch, and B-Branch fish ladders were dewatered and taken out of service for winter maintenance on 05 December.  Salmonids recovered included 158 O. mykiss, six chinook, and two coho.  Also recovered were 111 peamouth, 85 shad, 17 suckers, 15 whitefish, 13 lamprey, five northern pikeminnow, three smallmouth bass, and three carp.  Bonneville Fisheries thanks everyone who participated to make the process efficient and safe.   
3.  RESEARCH
3.1 Battelle/Normandeau.  Sensor fish postponed until further notice.

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 WDFW Chum.  Trapping and tagging continues.

3.4 WDFW Fish Counting.  16-hr video counting at Cascades Island, Washington Shore and Bradford Island.

4.  FISHWAYS

4.1 Project biologists inspected 06 through 09 December.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Will repair in 06/07
	

	All Week
	DSM2 
	Airburst OOS
	PLC failure
	TR sent to electricians.
	06-8326

	All Week
	B-Branch 
	North gate closed
	Separated from shaft
	See 6.1.4
	

	12/4
	PH1 N PCC
	Velocity <1.5 fps
	Slow water
	Normal condition.
	

	12/6
	Weir 38
	Reading <1.0>
	Clogged trashrack
	Riggers cleaned trashrack.
	

	12/6
	Weir 37
	Reading <1.0>
	Clogged trashrack
	Riggers cleaned trashrack.
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  Temperatures are not recorded during the winter maintenance period.

4.4 Sensor Calibration.  Calibration was not checked this week.  PH1 collection channel and B-Branch are out of service.  B-Branch and Cascades Island are out of calibration until sensors can be replaced and recalibrated.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B2CC PIT Tag Detector.  Demolition and construction continue.

5.2 B2 VBS modifications.  Gatewell VBS slot modifications continue on Unit 13.

5.3 Bradford Island Adult PIT Tag Detectors.  Installation began this week.

5.4 Main Unit Circuit Breaker.  Mods continue on Units 13.  Unit 14 returned to service on 08 December.  

5.5 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.6 SMF Full flow PIT Tag Detectors.  No new updates.

6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.
6.1.3 B-Branch north gate has separated from the shaft.  The south gate compensates when possible.  

6.1.4 Bradford Island, A-Branch, and B-Branch were dewatered and taken out of service for winter maintenance on 05 December.

6.2 Juvenile Fishways.
6.2.1 DSM2 screen cleaners in auto and on three hour cleaning cycles.  Airburst system in manual.  

6.3 Upcoming Events.
6.3.1 PH1 and PH2 STS removal on 15-16 December.

6.3.2 PH1 DSM dewatering on 19 December.

6.3.3 PH2 DSM dewatering on 20 December.

6.3.4 Two-mile pipe inspection on 20-21 December.

7.  HAZMAT, SPILLS AND CLEANUP.  Nothing to report
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.  
8.1 A teletype issued on 10 November requests hard tailwater constraint of 11.3’ to 11.7’ between 0700 and 1900 daily and no less than 11.3’ at any time.  This is to facilitate chum spawning around Ives and Pierce Islands.

8.2 A teletype issued on 05 December requests the following tailwater adjustments to occur on 06 December and 08 December.  This request is for chum spawning studies.  The objective is to achieve desired tailwater as quickly and smoothly as possible and to hold that elevation for the time requested.  The study is looking at how flow velocity affects chum spawning behaviour.  Once 11.5’ msl is reached, return to guidance per TTY RCC R 111005 1546 CO, Tailwater operation for chum spawning (see 8.1).  If target TW elevations cannot be reached, the Project is to hold TW as high as possible.
8.2.1 06 December tailwater elevations are as follows:
8.2.1.1 1600 increase from 11.5’ to 13.5’

8.2.1.2 1700 increase from 13.5’ to 15.5’

8.2.1.3 0100 decrease from 15.5’ to 13.5’

8.2.1.4 0200 decrease from 13.5’ to 11.5’

8.2.2 08 December tailwater elevations are as follows:

8.2.2.1 1600 increase from 11.5’ to 13.5’

8.2.2.2 2400 decrease from 13.5’ to 11.5’

JAMES R. MAHAR, P.E.

Operations Manager

//S/
1

