CENWP-OP-B                                                                                                                                  30 January 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 04 of 2006, which covers the period from 22 through 28 January 2006.

1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 162.0 to 204.3 kcfs.  Daily average project tailwater elevation ranged from 16.5’ to 19.9’ msl.  Daily average powerhouse forebay elevation ranged from 72.4’ to 74.0’ msl.  Daily average river temperature was 42(F.  Secchi disk measurements averaged 2.0 to 5.5 feet.

1.2 Daily average spill averaged 0.5 to 0.6 kcfs.   Spill Bay 1, which supplies attraction flow for Cascades Island, is open 6” during daylight hours.   

1.3 Unit operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.  

1.3.3 Unit 10 remains out of service for turbine rehab.

1.3.4 Unit 11 remains out of service due to a rotor failure.

1.3.5 Unit 12 went out of service at 0735 on 25 January for VBS modifications.
1.3.6 Unit 13 returned to service at 1700 on 26 January. 

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

1.4.1 F1 went out of service at 0408 on 23 January for annual maintenance.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves remain closed this reporting week.

2.1.1 FV1-1- for BI fishway overhaul.

2.1.2 FV3-7- for BI fishway overhaul.

2.1.3 FV3-9- for BI fishway overhaul.

2.1.4 FV4-3- for BI fishway overhaul.

2.1.5 FV4-4- for BI fishway overhaul.

2.2 STS/VBS Inspections.  STSs/VBSs have been removed for the winter.

2.3 Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week. 
2.3.1 On 26 January, biologists removed 15 yearling chinook, three stickleback, one sculpin and two juvenile carp from the Unit 12 draft tube.  One chinook was severely descaled, all other fish were in good condition and released at the Hamilton Island boat ramp.
3.  RESEARCH
3.1 Battelle/Normandeau.  Sensor fish testing scheduled for mid to late March.
3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 USGS.  Set lining and angling in forebay as part of the BI remediation will resume in mid-February.

3.4 WDFW Fish Counting.  16-hr video counting at Cascades Island and Washington Shore.  

4.  FISHWAYS

4.1 Project biologists inspected 23, 24, and 26 January.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Will repair in 06/07
	

	All week
	Cascades Is.
	FG6-12 closed
	Bent shaft
	Will repair in 06/07
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Temperatures are not recorded during the winter maintenance period.

4.4 Sensor Calibration.  PH1 collection channel and B-Branch are out of service.  Cascades Island is out of calibration until sensors can be replaced and recalibrated.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B1 ITS Wall Removal.  A letter report is expected in 2006.

5.2 B2CC PIT Tag Detector.  Construction continues.
5.3 B2 VBS modifications.  Mod started on Unit 12.

5.4 B2 Fish Unit trashrake.  According to the structural crew, the new rake does not work as well as the old rake.  The new rake is not being used at this time.

5.5 Bradford Island Adult PIT Tag Detectors.  Installation continues.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.7 SMF Full flow PIT Tag Detectors.  Pre-con meeting scheduled for 31 January.  Flume ovality and invert measurements scheduled for 01-14 February.  
6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Cascades Island PLC is in manual.  New sensors will be installed and calibrated before fish passage season for both CI and B-Branch.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  
6.1.3 PH2 PCC floating orifice gate stab plates were installed the week of 05 January.  Criteria is not maintained with just stab plates and one fish unit.  Diffusers and entrance gates have been adjusted to maintain a 1.0’ head over the monolith entrances.
6.1.4 Electricians are removing electrical hardware associated with PH1 PCC OG/SGs.
6.2 Juvenile Fishways.
6.2.1 DSM1 remains out of service until 15 September.

6.2.2 DSM2 remains out of service until late February.

6.3 Upcoming Events.
6.3.1 F1 returns to service around 02 February.  Stab plates will be removed at that time.
6.3.2 BI returns to service on 23 February.

7.  HAZMAT, SPILLS AND CLEANUP.  Nothing to report
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.  
8.1 A teletype issued on 31 December authorizes a minimum tailwater of 11.5’ for all hours, starting at 0000 on 01 January.  This operation is to provide chum incubation flows below Bonneville.

8.2 A teletype issued on 24 January requests a maximum tailwater of 21.0’ from 0700 on 24 January until 2100 on 27 January.  This is to facilitate concrete work at the B2CC.

8.3 A teletype issued on 30 January requests a tailwater of 16.5’ as a hard constraint, on 04 February.  This is to facilitate the installation of the SLADDs (sea lion acoustical deterrent devices).

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

