CENWP-OP-B                                                                                                                                  06 February 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 05 of 2006, which covers the period from 29 January through 04 February 2006.
1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 150.6 to 206.6 kcfs.  Daily average project tailwater elevation ranged from 15.7’ to 20.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.1’ to 74.9’ msl.  Daily average river temperature was 42(F.  Secchi disk measurements averaged 4.0 to 5.0 feet.

1.2 Daily average spill averaged 0.5 to 0.6 kcfs.   Spill Bay 1, which supplies attraction flow for Cascades Island, is open 6” during daylight hours.   

1.3 Unit operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.  

1.3.3 Unit 10 remains out of service for turbine rehab.

1.3.4 Unit 11 remains out of service due to a rotor failure.

1.3.5 Unit 12 remains out of service for VBS modifications.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

1.4.1 F1 returned to service at 1636 on 01 February.  F1 was out of service from 0600 until 1140 on 02 February for stab plate removal.
1.4.2 F2 was out of service from 0600 until 1140 on 02 February for stab plate removal.
1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves remain closed this reporting week.

2.1.1 FV1-1- for BI fishway overhaul.

2.1.2 FV3-7- for BI fishway overhaul.

2.1.3 FV3-9- for BI fishway overhaul.

2.1.4 FV4-3/ 4-4- for BI fishway overhaul.

2.2 STS/VBS Inspections.  STSs/VBSs have been removed for the winter.

2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week. 
3.  RESEARCH
3.1 Battelle/Normandeau.  Sensor fish testing scheduled for mid to late March.
3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA Fisheries lamprey.  Permanent installation of the BI AWS lamprey ramp to begin on 06 February.

3.4 USGS.  Set lining and angling in forebay as part of the BI remediation will resume in mid-February.

3.5 WDFW Fish Counting.  16-hr video counting at Cascades Island and Washington Shore.  

4.  FISHWAYS

4.1 Project biologists inspected 30-31 January and 2-3 February.
4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper install.
	Will repair in 06/07
	

	All week
	Cascades Is.
	FG6-12 closed
	Bent shaft
	Will repair in 06/07
	

	1/30
	Weir 37/38
	Reading <1.0’
	Unknown
	No response
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Temperatures are not recorded during the winter maintenance period.

4.4 Sensor Calibration.  PH1 collection channel and B-Branch are out of service.  Cascades Island is out of calibration until sensors can be replaced and recalibrated.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B1 ITS Wall Removal.  A letter report is expected in 2006.

5.2 B2CC PIT Tag Detector.  Construction continues.
5.3 B2 VBS modifications.  Mod continue on Unit 12.

5.4 B2 Fish Unit trashrake.  According to the structural crew, the new rake does not work as well as the old rake.  The new rake is not being used at this time.

5.5 Bradford Island Adult PIT Tag Detectors.  Installation continues.

5.6 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.7 SMF Full flow PIT Tag Detectors.  Pre-con meeting occurred on 31 January.  Flume invert measurements are scheduled for 06-14 February.  
6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Cascades Island PLC is in manual.  New sensors will be installed and calibrated before fish passage season for both CI and B-Branch.
6.1.2 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  
6.1.3 PH2 PCC floating orifice gate stab plates were removed on 02 February.
6.2 Juvenile Fishways.
6.2.1 DSM1 remains out of service until 15 September.

6.2.2 DSM2 remains out of service until late February.

6.3 Upcoming Events.
6.3.1 BI returns to service on 23 February.

7.  HAZMAT, SPILLS AND CLEANUP.  Nothing to report
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.  
8.1 A teletype issued on 31 December authorizes a minimum tailwater of 11.5’ for all hours, starting at 0000 on 01 January.  This operation is to provide chum incubation flows below Bonneville.

8.2 A teletype issued on 30 January requests a tailwater of 16.5’ as a hard constraint, on 04 February.  This is to facilitate the installation of the SLADDs (sea lion acoustical deterrent devices).

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

