CENWP-OP-B                                                                                                                                  27 March 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 12 of 2006, which covers the period from 19 through 25 March 2006.
1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 115.3 to 178.3 kcfs.  Daily average project tailwater elevation ranged from 11.9’ to 15.8’ msl.  Daily average powerhouse forebay elevation ranged from 74.0’ to 75.7 msl.  Daily average river temperature ranged from 43 to 44(F.  Secchi disk measurements averaged 5.0 to 6.0 feet.
1.2 Daily average spill averaged 1.2 to 1.4 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 0.5’ during daylight hours.
1.3 Unit Operation.
1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 10 remains out of service for turbine rehab.

1.3.4 Unit 11 remains out of service due to a rotor failure.

1.3.5 Unit 12 remains out of service for VBS modifications.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week.  
2.1.1 FV5-9 closed at 1655 on 21 March for Cascades Is. dewatering.

2.2 STS/VBS Inspections.   No STSs/VBSs were inspected this reporting week.  
2.3 Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.
2.3.1 On 22 March, the Cascades Island exit section was closed and dewatered.  Three adult steelhead and two juvenile salmonids were moved downstream of the picketed leads.  All were in excellent condition.
3.  RESEARCH
3.1 Battelle/Normandeau.  Sensor fish testing from 23 - 25 March.
3.2 ERDC TDG.  Sensors remain installed in the tailrace.
3.3 NOAA Fisheries lamprey.  Permanent installation of the BI AWS lamprey ramp completed.
3.4 PSMFC.  No adult salmonids were observed crossing the separator bars this week.
3.5 USDA Wildlife Services.  Sea lion hazing continues using 15mm cracker/screamer shells and rubber bullets.

3.6 WDFW Fish Counting.  16-hr video counting at Bradford Island and Washington Shore.   
3.7 Fish Field Unit.  Sea lion observation and acoustic deterrent evaluations continue.
4.  FISHWAYS 

4.1 Project biologists inspected 19 March – 25 March.
4.2 Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper installation
	Will repair in 06/07
	

	All week
	Cascades Is.
	FG6-12 closed
	Bent shaft
	Will repair in 06/07
	

	All week
	PH1 CCH Diffusers
	FG2-22A closed, 2-19 stuck half open
	Unknown.  Failed during water up.
	Will repair in 07/08
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  
	Date
	Wash. Shore
	Bradford Is.

	3/19
	43.0
	43.2

	3/20
	43.3
	43.5

	3/21
	43.6
	43.7

	3/22
	43.6
	43.8

	3/23
	43.9
	44.1

	3/24
	44.2
	44.3

	3/25
	44.5
	44.7


4.4 Sensor Calibration.  Calibration was checked on 25 March.  Cascades Is.  needs to be recalibrated.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5.   CONSTRUCTION

5.1 B1 ITS Wall Removal.  A letter report is expected in 2006.

5.2 B2CC PIT Tag Detector.  Installation began on 23 March.  Final walk through scheduled for 07 April.
5.3 B2 VBS modifications.  Mods continue on Unit 12.  
5.4 B2 Fish Unit trash rake.  According to the structural crew, the new rake does not work as well as the old rake and is not being used at this time.

5.5 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.6 SMF Full flow PIT Tag Detectors.  Construction continues.
6.  FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island PLC’s are in manual.  
6.1.2 New sensors for B-branch and Cascades Island tailrace, entrance and ladder have been installed. 
6.1.3 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07. 
6.1.4 SLADDs and SLEDs are installed at all fishway entrances. 
6.1.5 The UMT was put into service at 1030 on 22 March.  Cascades Is. exit section is out of service with the exit closed.  Video counting at Cascades Is. has concluded.
6.2 Juvenile Fishways.
6.2.1 DSM1 remains out of service until 15 September.
7.  HAZMAT, SPILLS AND CLEANUP - Nothing to report.
8.  TELETYPES AND OTHER NOTEWORTHY ITEMS.  
8.1 A teletype issued on 31 December authorizes a minimum tailwater of 11.5’ for all hours, starting at 0000 on 01 January until further notice.  This operation is to provide chum incubation flows below Bonneville.

8.2 The navigation lock returned to service at 1130 on 24 March.
8.3 A single sea lion was observed in the WA shore ladder this reporting week.  
JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

