CENWP-OP-B                                                                                                                                  10 April 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 14 of 2006, which covers the period from 02 April through 08 April 2006.
1.  OPERATION SUMMARY

1.1 Daily average river flows ranged from 191.3 to 328.5 kcfs.  Daily average project tailwater elevation ranged from 16.6’ to 23.6’ msl.  Daily average powerhouse forebay elevation ranged from 73.4’ to 75.7 msl.  Daily average river temperature ranged from 47 to 48(F.  Secchi disk measurements averaged 3.0 to 5.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 0.5’ during daylight hours.  Spill started on 04 April at 1236 and continued all week with a range of 25 to 150 kcfs.  Daily average spill averaged 1.2 to 125.7 kcfs.
1.3 Unit Operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 10 remains out of service for turbine rehab.

1.3.4 Unit 11 remains out of service due to a bearing problem.

1.3.5 Unit 12 remains out of service for VBS modifications.
1.3.6 Unit 13 was out of service from 0758 until 1239 on 3 April due to VBS delivery.

1.3.7 Unit 14 had a 1% violation on 05 April due to STS inspections.
1.3.8 Unit 15 had a 1% violation on 05 April due to STS inspections.

1.3.9 Unit 16 had a 1% violation on 05 April due to STS inspections.

1.3.10 Unit 18 had a 1% violation on 05 April due to STS inspections.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

1.5 Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

2.  ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week.  
2.1.1 FV5-3 and 5-4 closed for removing fish net from intake screen from 1520 until 1535 on 04 April.   
2.2 STS/VBS Inspections.   The following STSs/VBSs were inspected this reporting week:
	Unit
	Date
	Run Hours
	Comments

	11
	 4/5
	5
	

	12
	
	
	

	13
	4/5
	643
	

	14
	4/5
	153
	

	15
	4/5
	653
	

	16
	  4/5
	650
	

	17
	4/5
	653
	

	18
	4/5
	653
	


2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.
RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.
3.2 Fish Field Unit.  Sea lion observation and acoustic deterrent evaluations continue.

3.3 NOAA Fisheries lamprey.  Permanent installation of the BI AWS lamprey ramp completed.
3.4 PSMFC.  25 adult steelhead were observed crossing the separator bars this week.  One steelhead kelt was removed from the separator bars and released alive.
3.5 U of I.  Trapping began this week in the AFF.

3.6 USDA Wildlife Services.  Sea lion hazing continues using 15mm cracker/screamer shells and rubber bullets.

3.7 WDFW Fish Counting.  Visual fish counting continues.
3.8 WDFW/ODFW.  Sea lion hazing from boats in the tailrace commenced on April 1st.  Hazers are not allowed in the inner BRZ.

3.  FISHWAYS 

4.1 Project biologists inspected 02 – 08 April.
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper installation
	Will repair in 06/07
	

	All week
	Cascades Is.
	FG6-12 closed
	Bent shaft
	Will repair in 06/07
	

	All week
	PH1 CCH Diffusers
	FG2-22A closed, 2-19 stuck half open
	Unknown.  Failed during water up.
	Will repair in 07/08
	

	All week
	PH2 SUE
	Entrance gate < 13’
	Unknown
	TR submitted for calibration
	06-29824

	4/2
	Casc. Is. entrance
	Differential low (0.6’)
	Power loss
	Power restored.
	

	4/8
	B-branch entrance
	Differential high
	Unknown
	Operator adjusted
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  
	Date
	Wash. Shore
	Bradford Is.

	4/2
	47.3
	47.4

	4/3
	47.5
	47.6

	4/4
	47.5
	47.6

	4/5
	48.0
	48.0

	4/6
	48.1
	48.2

	4/7
	48.0
	48.2

	4/8
	48.2
	48.3


4.4 Sensor Calibration.  Calibration was checked on 08 April.  
4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.   CONSTRUCTION

4.1 B1 ITS Wall Removal.  A letter report is expected in 2006.

4.2 B2CC PIT Tag Detector.  Final walk through occurred on 07 April.  Wet testing continues.
4.3 B2 VBS modifications.  VBS delivery occurred on 3 April.  
4.4 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

4.5 SMF Full flow PIT Tag Detectors.  Construction continues.
5.  FISHWAY STATUS

5.1  Adult Fishways.    
5.1.1 Bradford Island and Cascades Island PLC’s are in manual.  
5.1.2 New sensors for B-branch and Cascades Island tailrace, entrance and ladder have been installed. 
5.1.3 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07. 
5.1.4 SLADDs and SLEDs are installed at all fishway entrances. 
5.1.5 The Adult Fish Facility was watered-up on 01 April. 
5.2 Juvenile Fishways.
5.2.1 DSM1 remains out of service until 15 September.
6.  HAZMAT, SPILLS AND CLEANUP - Nothing to report.
7.  TELETYPES AND OTHER NOTEWORTHY ITEMS.  
7.1 A teletype issued on 31 December authorizes a minimum tailwater of 11.5’ for all hours, starting at 0000 on 01 January until further notice.  This operation is to provide chum incubation flows below Bonneville.
7.2 A teletype issued on 06 April authorized an exceedence of the normal summer 24-hour tailwater fluctuation    

        limit of 4.0 feet from 1200 hrs 06 April to 1200 hrs 07 April.  Tailwater is allowed to fluctuate up to 5’.

7.3   A teletype issued on 07 April authorized an exceedence of the normal summer 24-hour tailwater fluctuation    

              limit of 4.0 feet from 0900 hrs 08 April to 0900 hrs 09 April.  Tailwater is allowed to fluctuate up to 5’.


7.4   A teletype was issued on 07 April requesting 100 kcfs spill for juvenile fish beginning at 0001 hrs on 10    

              April
until further notice.

7.5   A teletype issued on 08 April requests that Bonneville provide no spill from 0700 to 1100 on 09 April to   

              complete dive work for sediment disposal work at Bradford Island.


7.6   A teletype was issues on 08 April allowing Bonneville two exceedences.  The normal summer 24-hour     

              tailwater fluctuation of 4’ can increase to 5’ from 0001 hrs on 09 April to 1700 on 10 April. The normal     

              forebay limit of 76’ can increase to 77’ from 0001 to 1700 on 10 April.

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

