CENWP-OP-B                                                                                                                                  01 May 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 17 of 2006, which covers the period from 23 April through 29 April 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 312.6 to 343.7 kcfs.  Daily average project tailwater elevation ranged from 23.4’ to 24.8’ msl.  Daily average powerhouse forebay elevation ranged from 73.3’ to 75.7 msl.  Daily average river temperature ranged from 50 to 52(F.  Secchi disk measurements averaged 2.5 to 3.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 83.4 to 120.1 kcfs.
1.3 Unit Operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 7 had a 1% violation from 1345 until 1600 on 26 April due to trash raking.
1.3.4 Unit 10 remains out of service for turbine rehab.

1.3.5 Unit 11 went out of service at 0714 on 24 April for bearing alignment.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

1.4.1 Fish Unit 1 and 2 were run at reduced load while removing SLEDS from 1058 until 1150 on 24 April.  See 6.1.4.  

1.4.2 Fish Unit 1 was out of service from 2333 on 28 April until 1142 on 29 April due to governor oil leak.  Fish Unit 2 was in standby from 0925 until 1130 on 29 April for repairs to Fish Unit 1.  See 6.1.5
1.5 Gatewell drawdowns are measured on Wednesdays.  VBS drawdowns are measured daily on Units 12, 13, and 17.

2 ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed this reporting week.     
2.2 STS/VBS Inspections.   No STSs/VBSs were inspected this reporting week.
2.3 Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week:
2.3.1
  Unit 11 draft tube – two adipose clipped adult chinook, two juvenile chinook, one juvenile sockeye,    and one peamouth.  All were released alive except for one adult chinook.  

3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF.  

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 Fish Field Unit.  Sea lion observation and acoustic deterrent evaluations continue.

3.4 NOAA Fisheries - juvenile salmonids.  Sampling juvenile salmonids to determine prevalence of pathogens.  

3.5 NOAA Fisheries - barge vs. bypass.   Assessment of the health of hatchery salmon relative to in-river and transportation life-histories.
3.6 PSMFC.  11 adult steelhead were observed crossing the separator bars this week.  25 yearling chinook and 25 coho were collected for NOAA researchers this reporting week. 
3.7 U of I.  Radio tagging of spring chinook for SLED evaluation continues in the AFF.

3.8 USDA Wildlife Services.  Sea lion hazing continues using 15mm cracker/screamer shells and rubber bullets.

3.9 WDFW Fish Counting.  Visual fish counting continues.
3.10 WDFW/ODFW.  Sea lion hazing from boats continues.

4 FISHWAYS 

4.1 Project biologists inspected 23 – 29 April. 
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH2 SCCH
	Velocity <1.5 fps
	Improper installation
	Will repair in 06/07
	

	All week
	Cascades Is.
	FG6-12 closed
	Bent shaft
	Will repair in 06/07
	

	All week
	PH1 CCH Diffusers
	FG2-22A closed, 2-19 stuck half open
	Unknown.  Failed during water up.
	Will repair in 07/08
	

	4/27
	B-Branch
	Entrance diff. >2.0
	In manual
	Adjusted FV4-3
	

	4/28-4/29
	NUE, NDE, SUE, SDE
	Entrance diff. < 1.0
	FOG and Fish Unit repair
	In criteria by 1142 on 4/29
	


Table 2.  FPP Out of Criteria items.

4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  
	Date
	Wash. Shore
	Bradford Is.

	4/23
	50.0
	50.1

	4/24
	50.4
	50.5

	4/25
	50.6
	50.9

	4/26
	50.6
	50.8

	4/27
	51.0
	51.2

	4/28
	51.4
	51.6

	4/29
	51.9
	52.0


4.4 Sensor Calibration.  Calibration was checked on 29 April.  
4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  A letter report is expected in 2006.

5.2 B2CC PIT Tag Detector.  Construction complete.  Opened for the season at 0815 on 13 April.
5.3 B2 VBS modifications.  VBS delivery occurred on 3 April.  
5.4 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.5 SMF Full flow PIT Tag Detectors.  Construction continues.
6 FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Bradford Island and Cascades Island PLC’s are in manual.  
6.1.2 New sensors for B-branch and Cascades Island tailrace, entrance and ladder have been installed. 
6.1.3 Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07. 
6.1.4 Floating Orifice Gates at PH2 were submerged due to cracking and leaking around the sea lion exclusion bars.   They are being repaired as time permits.
6.1.5 SLEDs were lifted above water level at the north and south downstream entrances of PH2 from 1150 on 24 April until 1210 on 26 April for a passage test.   SLADDs and SLEDs are installed at all fishway entrances.  See 1.4.1 
6.1.6 NUE entrance gate was closed and differential at PH2 was 1.3’ from 0044 until 0925 on 29 April.  Differential was 0.1’ from 0925 until 1130 on 29 April while Fish Unit 2 was in standby.  All PH2 entrances returned to normal operating condition by 1142 on 29 April.  See 1.4.2   
6.2 Juvenile Fishways.
6.2.1 DSM1 remains out of service until 15 September.
6.2.2 The B2CC remains open.  

7 HAZMAT, SPILLS AND CLEANUP - Nothing to report.
8 TELETYPES AND OTHER NOTEWORTHY ITEMS.   
8.1 A teletype was issued on 19 April setting the spill priority list for Columbia Basin projects and providing guidance for project operation for voluntary and involuntary spill.

8.2 A teletype was issued on 28 April indicating that for spill levels less than or equal to 92 kcfs, use the spill patterns sent to the project.  

JAMES R. MAHAR, P.E.

Operations Manager

//S/

1

