CENWP-OP-B                                                                                                                                  28 May 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 21 of 2006, which covers the period from 21 through 27 May 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 373.0 to 395.8 kcfs.  Daily average project tailwater elevation ranged from 26.4’ to 27.3’ msl.  Daily average powerhouse forebay elevation ranged from 74.5’ to 75.4 msl.  Daily average river temperature ranged from 59 to 60(F.  Secchi disk measurements averaged 2.8 to 4.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 149.4 to 167.8 kcfs.
1.3 Unit Operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 8 was out of service from 1540 until 1650 on 22 May due to a gross head failure alarm.

1.3.4 Unit 10 remains out of service for turbine rehab.

1.3.5 Unit 11 remains out of service for bearing alignment.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.5 Gatewell drawdowns are measured on Wednesdays.  VBS drawdowns are measured daily on Units 12, 13, and 17.

2 ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed this reporting week.           

2.2 STS/VBS Inspections.   No STSs/VBSs were inspected this reporting week.
2.3 Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.
3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF. 
3.2 CTUIR.  Collecting adult lamprey for continuation of Umatilla Basin lamprey re-introductions. 

3.3 ERDC TDG.  Sensors remain installed in the tailrace.

3.4 Fish Field Unit.  Sea lion observation and acoustic deterrent evaluations concluded on 27 May.

3.5 NOAA Fisheries.  Sampling juvenile salmonids to determine prevalence of pathogens.  

3.6 NOAA Fisheries.  Assessment of the health differences between barged and bypassed hatchery salmon.
3.7 PSMFC.  Five steelhead, 11 salmon were observed crossing the separator bars.  614 clipped yearling chinook and 25 coho were collected for NOAA researchers. 
3.8 U of I.  Radio tagging of spring chinook for SLED evaluation will conclude on 1 June.  South Fork Salmon R. and shad sampling will continue through late July.   
3.9 USDA Wildlife Services.  Sea lion hazing concluded on 25 May. 

3.10 WDFW Fish Counting.  Visual fish counting continues.
3.11 WDFW/ODFW.  Sea lion hazing from boats concluded on 23 May.

4 FISHWAYS 

4.1 Project biologists inspected 21 through 27 May 2006.
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	SUE/SDE
	Gate < 13’
	Unknown
	WAR submitted
	06-37661

	All week
	A&B Branches
	Reading > 1.3’
	See 6.1.3
	WAR submitted
	06-37659

	5/25
	DSM2
	ERG tripped
	Debris loads
	See 6.2.2
	06-37174


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed in the winter of 04/05.

4.2.3 Cascades Island FG6-12 is closed due to a bent shaft.  Repairs can not be made until winter 06/07.

4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  For now, the collection channel is operating within FPP criteria.
4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  
	Date
	Wash. Shore
	Bradford Is.

	5/21
	59.1
	59.2

	5/22
	59.3
	59.3

	5/23
	59.4
	59.4

	5/24
	59.6
	59.6

	5/25
	59.7
	59.7

	5/26
	59.4
	59.4

	5/27
	59.0
	58.9













Table 3.  Bonneville Fishway temperatures
4.4 Sensor Calibration.  Calibration was checked on 26 May.  Several sensors are reading low.
4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  A letter report is expected in 2006.

5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.3 SMF Full flow PIT Tag Detectors.  Construction continues.
6 FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Cascades Island PLC is in manual.  
6.1.2 A couple of PH2 floating orifice gates appear to be slightly stuck.  There is about two inches of water leaking over the tops.
6.1.3 Due to high tailwater, B-branch staff gauge is submerged.  A-branch is reading .1-.3’ high due to the BI weir reading 1.2’-1.3’ as is normal for shad passage mode.  A WAR was submitted to reduce elevations at BI to 1.1’-1.2’.
6.2 Juvenile Fishways.
6.2.1 DSM1 remains out of service until 15 September.
6.2.2 On 25 May, from 1504 until 1520, the ERG tripped due to high water elevations from a build up of debris in the DSM.  The airburst system is set to run every 20 minutes, but is not fully functional due to some problems caused by programming earlier this spring.  As of 0310 on 24 May, DSM2 screen cleaner #1 remains out of service.  A TR for repair was submitted (TR# 06-37174).  

6.2.3 DSM2 orifices F2A-N and F2B-N were closed on 27 May.
6.2.4 Several dozen gulls were observed at the outfall this past week.  Currently, there are no hazing efforts at the outfall.

7 HAZMAT, SPILLS AND CLEANUP - Nothing to report.
8 TELETYPES AND OTHER NOTEWORTHY ITEMS. 
8.1 A teletype issued on 26 May requesting to keep Bonneville pool greater than 74.0 feet as a soft constraint if The Dalles’ average flow is expected to be greater than 250 kcfs.  
8.2 Teletypes issued on 25 and 26 May request a 75.5’ msl, hard constraint, forebay when flows are expected to be greater than 376 kcfs.  This is to keep space in the forebay during high flow conditions.

JAMES R. MAHAR, P.E.

Operations Manager

1

