CENWP-OP-B                                                                                                                                  04 June 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 22 of 2006, which covers the period from 28 May through 03 June 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 402.9 to 323.3 kcfs.  Daily average project tailwater elevation ranged from 23.7’ to 27.7’ msl.  Daily average powerhouse forebay elevation ranged from 74.7’ to 75.7 msl.  Daily average river temperature ranged from 57 to 59(F.  Secchi disk measurements averaged 2.0 to 3.2 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 102.6 to 179.0 kcfs.
1.3 Unit Operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 10 remains out of service for turbine rehab.

1.3.4 Unit 11 remains out of service for bearing alignment.
1.3.5 Unit 12 had reduced load at 2115 on 28 May due to VBS drawdowns.   Unit 12 had a 1% violation on 01 June due to STS inspections.

1.3.6 Unit 13 VBSs were cleaned from 1336 until 1406 on 31 May.  Unit 13 had a 1% violation on 01 June due to STS inspections.

1.3.7 Unit 14 had a 1% violation on 01 June due to STS inspections.
1.3.8 Unit 15 had a 1% violation on 01 June due to STS inspections.
1.3.9 Unit 16 had a 1% violation on 01 June due to STS inspections.
1.3.10 Unit 17 had a 1% violation on 01 June due to STS inspections.
1.3.11 Unit 18 had a 1% violation on 01 June due to STS inspections.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.5 Gatewell drawdowns are measured on Wednesdays.  VBS drawdowns are measured daily on Units 12, 13, and 17.

2 ACTIVITIES

2.1 AWS Closures. The following AWS valves were closed this reporting week.           
2.1.1 FV3-9 was closed for cleaning from 0731 until 0741 on 30 May
2.2 STS/VBS Inspections.   The following STSs/VBSs were inspected this reporting week.
	Unit
	Date
	Run Hours
	Comments

	11
	 6/1
	138
	

	12
	6/1
	719
	Repaired dogging mechanism 

	13
	6/1
	751
	

	14
	6/1
	753
	

	15
	6/1
	752
	

	16
	6/1
	753
	

	17
	6/1
	752
	

	18
	6/1
	749
	


Table 1.  STS and VBS video inspections.

2.3 Dewatering and Fish Salvage.  The following dewatering activities occurred this reporting week.
2.3.1 DSM2 was bulkheaded and the ERG opened on 31 May.  Seven dead, adult chinook were found at the separator bars.  Please see 6.2.4 and 6.2.5 for more details.
3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF. 

3.2 CTUIR.  Collecting adult lamprey for continuation of Umatilla Basin lamprey re-introductions. 

3.3 ERDC TDG.  Sensors remain installed in the tailrace.

3.4 NOAA Fisheries.  Sampling juvenile salmonids to determine prevalence of pathogens.  

3.5 NOAA Fisheries.  Assessment of the health differences between barged and bypassed hatchery salmon.
3.6 PSMFC.  One steelhead and one salmon were observed crossing the separator bars.  202 clipped yearling chinook and 25 coho were collected for NOAA researchers.
3.7 PSMFC PIT tag.  Monthly testing of the B2CC detectors starting 06 June through October.
3.8 U of I.  Radio tagging of spring chinook for SLED evaluation concluded on 1 June.  South Fork Salmon R. and shad sampling continues through late July.   
3.9 WDFW Fish Counting.  Visual fish counting continues.

4 FISHWAYS 

4.1 Project biologists inspected 28 May through 03 June 2006.
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	5/28-30
	SUE/SDE
	Gate < 13’
	Unknown
	WAR submitted
	06-37661

	5/29
	A&B Branches
	Reading > 1.3’
	See 6.1.2
	WAR submitted
	06-37659

	5/28
	FG6-20
	Incorrect position
	In manual
	Operators adjusted.
	

	5/29
	FG6-14
	Incorrect position
	 In manual
	Operators adjusted.
	

	5/29
	DSM2
	ERG tripped
	debris on screens
	See 6.2.3
	

	5/31
	DSM2
	ERG open
	SC #1 repair
	See 6.2.4
	

	5/31
	NDE
	Closed
	Lamprey ramp work
	See 6.1.2
	


Table 2.  FPP Out of Criteria items.
4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed in the winter of 04/05.

4.2.3 Cascades Island FG6-12 is closed due to a bent shaft.  Repairs can not be made until winter 06/07.

4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  For now, the collection channel is operating within FPP criteria.
4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  
	Date
	Wash. Shore
	Bradford Is.

	5/28
	58.4
	58.3

	5/29
	57.9
	57.9

	5/30
	57.8
	57.8

	5/31
	57.6
	57.7

	6/1
	57.6
	57.6

	6/2
	57.6
	57.6

	6/3
	58.1
	58.1













Table 3.  Bonneville Fishway temperatures
4.4 Sensor Calibration.  Calibration was checked on 03 June.  
4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  A letter report is expected in June 2006.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.3 SMF Full flow PIT Tag Detectors.  Construction should be completed by mid-June.  Electronics installation begins in early June.  The entire system should be online by mid to late June.
6 FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Cascades Island PLC is in manual.  
6.1.2 Due to high tailwater, B-branch staff gauge is submerged.  A-branch reads high due to the BI weir reading 1.2’-1.3’, as is normal for shad passage mode.  The BI weir was reset on 30 May to 1.1’-1.2’.  
6.1.3 NDE, at the PH2 north monolith, was closed from 1217 until 1320 on 31 May to facilitate work on the lamprey ramp.
6.2 Juvenile Fishways.
6.2.1 DSM1 remains out of service until 15 September.
6.2.2 Several dozen gulls were observed at the outfall this past week.  Currently, there are no hazing efforts at the outfall.
6.2.3 On 29 May, from 1800 until 1830, the ERG was open.  The ERG had tripped due to high water elevations from a build up of debris on the DSM screens.  As of 0310 on 24 May, DSM2 screen cleaner #1 remains out of service.  A TR for repair was submitted (TR# 06-37174).  
6.2.4 Screen cleaner #1 repairs were performed on 31 May.  To facilitate repairs, the ERG was opened at 0718, the bulkhead installed at 0735.  Flushing water automatically flushed the two mile pipe for 30 minutes.  Repairs were completed and the bulkhead pulled at 1331.  The ERG was closed at 1353 and the mechanical screen sweeps put into auto mode with a six hour cleaning cycle.  The airburst system is on heavy mode with a 20 minute cleaning cycle. 
6.2.5 Upon water up of the two mile pipe on 31 May, PSMFC reported seven dead adult chinook on the separator bars.  It is suspected these fish may have held in the two mile pipe after the flushing water turned off.  In the future, Project biologists will manually operate the flushing water to flow continuously during in-season dewaterings by placing the flushing valve in Manual and Open.
7 HAZMAT, SPILLS AND CLEANUP - Nothing to report.
8 TELETYPES AND OTHER NOTEWORTHY ITEMS. 
8.1 Teletypes issued on 25 and 26 May request a 75.5’ msl, hard constraint, forebay when flows are expected to be greater than 376 kcfs.  This is to keep space in the forebay during high flow conditions.  This teletype was cancelled on 02 June.
8.2 A teletype issued on 31 May requests a maximum spill of 150 kcfs from 1000-1200 on 01 June.  This is to facilitate equipment installation in the BRZ.

8.3 A fish memo, detailing the dead adult chinook, was sent to CENWP-OD biologists Cal Sprague and Randy Bailey on 03 June.

JAMES R. MAHAR, P.E.

Operations Manager

1

