CENWP-OP-B                                                                                                                                  16 July 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 28 of 2006, which covers the period from 09 through 15 July 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 176.6 to 233.5 kcfs.  Daily average project tailwater elevation ranged from 15.3’ to 18.7’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 76.4 msl.  Daily average river temperature ranged between 68( and 70(F.  Secchi disk measurements averaged 4.5 to 6.5 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 89.2 to 92.3 kcfs.
1.3 Unit Operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 10 remains out of service for turbine rehab.

1.3.4 Unit 12 was out of service from 0838 until 1133 on 12 July for URX replacement.  Unit 12 went out of service at 0458 on 15 July due to exciter problems.
1.3.5 Unit 14 was out of service from 0440 until 1926 on 14 July due to high lift pump trouble.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed for cleaning.
2.1.1 FV3-7 from 0650 until 0730 on 10 July.

2.1.2 FV3-9 from 0650 until 0730 on 10 July.

2.1.3 BI exit from 0700 until 0715 on 10 July.
2.2 STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.
2.3 Dewatering and Fish Salvage.  No dewatering activities occurred this reporting week.
3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF.  

3.2 CTUIR.  Collecting adult lamprey for continuation of Umatilla Basin lamprey re-introductions. 

3.3 ERDC TDG.  Sensors remain installed in the tailrace.

3.4 NOAA Fisheries- Gilbreath.  Salt water rearing subyearling chinook at the SMF continues.    
3.5 NOAA Fisheries- McComas.  Acoustic tagging in the SMF continues.
3.6 NOAA Fisheries lamprey.  Fish collection and monitoring continues until September.  
3.7 PSMFC smolt monitoring.  685 subyearling chinook were collected for NOAA researchers.  
3.8 PSMFC PIT tag.  Monthly testing of the B2CC detectors June through October.
3.9 PSMFC/USDA.  Pikeminnow angling from the project and in the tailrace BRZ.
3.10 U of I adults.  South Fork Salmon R. and shad sampling concluded on 14 July.   

3.11 U of I lamprey.  Collection and testing continue
3.12 WDFW Fish Counting.  Visual fish counting continues.
4 FISHWAYS 

4.1 Project biologists inspected 09 through 15 July 2006.  
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	DSM2 airburst
	Five screens not working.
	Electrical
	See 6.2.3
	06-40863

	7/14
	B-Branch
	FG3-24
	System in manual
	Operators closed.
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed in the winter of 04/05.

4.2.3 Cascades Island FG6-12 is closed due to a bent shaft.  Repairs can not be made until winter 06/07.

4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  For now, the collection channel is operating within FPP criteria.
4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  
	Date
	WS avg.
	BI avg.
	AFF max
	SMF max

	7/09
	68.7
	68.5
	68.7
	67.7

	7/10
	69.0
	69.0
	69.0
	68.1

	7/11
	69.1
	69.1
	69.1
	68.2

	7/12
	68.9
	68.9
	68.9
	68.0

	7/13
	69.1
	69.0
	69.1
	68.1

	7/14
	69.7
	69.6
	69.7
	68.9

	7/15
	70.0
	69.9
	70.0
	69.1


Table 3.  Bonneville Fishway temperatures
4.4 Sensor Calibration.  Calibration was checked on 15 July.  
4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  A letter report was issued and a meeting held on 11 July.  Comment period is open for two weeks.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.3 SMF Full flow PIT Tag Detectors.  Construction completed.  System ready to be tested with PIT tags.
6 FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Cascades Island PLC is in manual.  
6.1.2 Shad numbers have decreased enough to allow the AFF to continue with normal operation of the picket leads.   Please see 8.4
6.1.3 Due to temperatures at the AFF reaching 70(F, trapping is limited to every other day with no more than four days/week.
6.2 Juvenile Fishways.
6.2.1 DSM1 remains out of service until 15 September.
6.2.2 TIES remain installed.

6.2.3 DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  The Project is waiting on contractors before repairs may be completed.

6.2.4 There are adult fish in the DSM2 add-in water.  Biologists are attempting to net fish out whenever possible.
6.2.5 Removal and repair of the spare STS is scheduled for the week of 17 July.
7 HAZMAT, SPILLS AND CLEANUP - Nothing to report.
8 TELETYPES AND OTHER NOTEWORTHY ITEMS. 
8.1 A teletype sent on 28 June requests that Bonneville start summer spill of 75 KCFS during daytime hours and spill to the 120% gas cap at night until further notice.
8.2 A teletype sent on 07 July requests a soft constraint of 75.5’ to 76.5’, and a hard constraint of 75.0’ to 76.5’, on the Bonneville pool from 0600, 10 July to 1800, 13 July.  A request send on 12 July extends the forebay constraints from 0600 on 17 July until 1800 on 20 July and from 0600 on 24 July until 1800 on 27 July.  These requests are to limit wear and tear on gill nets due to pool fluctuations.
8.3 A teletype sent on 13 July requests a soft forebay constraint of 75.0’ – 76.5’ from 0600 until 1800 everyday from 24-29 July.  This operation is necessary for SDS Lumber to maneuver a barge for rock placement.  Additional teletypes will be issued, as needed, until the work is completed in late August.
8.4 At the 14 July FPOM meeting, a modification to FPP Appendix G was proposed. The change will state that only two picket leads should be lowered at anytime.  Additional leads may be lowered if needed and coordinated with Project Fisheries and FPOM.
JAMES R. MAHAR, P.E.

Operations Manager

1

