CENWP-OP-B                                                                                                                                  24 July 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 29 of 2006, which covers the period from 16 through 22 July 2006.
1 OPERATION SUMMARY
1.1 Daily average river flows ranged from 158.8 to 195.2 kcfs.  Daily average project tailwater elevation ranged from 14.3’ to 16.2’ msl.  Daily average powerhouse forebay elevation ranged from 74.2’ to 76.6 msl.  Daily average river temperature ranged between 69( and 71(F.  Secchi disk measurements averaged 4.7 to 7.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 86.6 to 92.3 kcfs.
1.3 Unit Operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 10 remains out of service for turbine rehab.

1.3.4 Unit 12 returned to service at 1204 on 18 July.  Unit 12 was out of service from 1317 until 1330 on 18 July due to an emergency shutdown for URX trouble. 
1.3.5 Unit 15 was out of service from 0310 until 1353 on 17 July for transformer bank outage.
1.3.6 Unit 16 was out of service from 0310 until 1353 on 17 July for transformer work.

1.3.7 Unit 17 was out of service from 0310 on 17 July until 1702 on 19 July for transformer work.
1.3.8 Unit 18 was out of service from 0301 until 1334 on 17 July for a bank outage.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed.
2.2 STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.
2.3 Dewatering and Fish Salvage.  No dewatering activities occurred this reporting week.
3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF.  Four day restriction due to temperatures reaching 70(F
3.2 CTUIR.  Currently at 549 out of 560 fish for Umatilla Basin re-introductions.   
3.3 ERDC TDG.  Sensors remain installed in the tailrace.

3.4 NOAA Fisheries- Gilbreath.  Salt water rearing subyearling chinook at the SMF continues.    

3.5 NOAA Fisheries- McComas.  Acoustic tagging in the SMF continues.

3.6 NOAA Fisheries lamprey.  Sampling on hold due to water temperatures.
3.7 PSMFC smolt monitoring.  Processing fish more often due to temperatures reaching 70(F.   368 subyearling chinook were collected for NOAA researchers.  
3.8 PSMFC PIT tag.  Monthly testing of the B2CC detectors June through October.
3.9 PSMFC/USDA.  Pikeminnow angling from the project and in the tailrace BRZ.

3.10 U of I lamprey.  Testing will conclude on 23 July.
3.11 WDFW Fish Counting.  Visual fish counting continues.
4 FISHWAYS 

4.1 Project biologists inspected 16 through 22 July 2006.  
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	DSM2 airburst
	Five screens not working.
	Electrical
	See 6.2.3
	06-40863

	7/17, 7/19
	Weir 37 
	Reading <1.3’>
	Unknown
	Screen cleaned.
	

	7/17-22
	PH2 FB
	TIES in unit 14
	Moved for barge access
	TIES scheduled for removal on 23 July.
	

	7/19, 7/22
	Weir 38
	Reading <1.3’>
	AFF operations
	No action taken
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed in the winter of 04/05.

4.2.3 Cascades Island FG6-12 is closed due to a bent shaft.  Repairs can not be made until winter 06/07.

4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  For now, the collection channel is operating within FPP criteria.
4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  
	Date
	WS avg.
	BI avg.
	AFF max
	SMF max

	7/16
	70.4
	70.3
	70.4
	69.5

	7/17
	70.1
	70.0
	70.1
	69.2

	7/18
	69.6
	69.5
	69.6
	68.7

	7/19
	69.6
	69.6
	69.6
	68.8

	7/20
	70.0
	69.9
	69.9
	69.1

	7/21
	70.7
	70.4
	70.7
	69.8

	7/22
	71.5
	71.3
	71.5
	70.6


Table 3.  Bonneville Fishway temperatures
4.4 Sensor Calibration.  Calibration was checked on 16 July.  
4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Comment period is open for two weeks.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.3 SMF Full flow PIT Tag Detectors.  Construction completed.  System ready to be tested with PIT tags.
6 FISHWAY STATUS

6.1  Adult Fishways.    
6.1.1 Cascades Island PLC is in manual.  
6.1.2 Due to temperatures at the AFF reaching 70(F, trapping is limited to every other day with no more than four days/week.
6.2 Juvenile Fishways.
6.2.1 DSM1 remains out of service until 15 September.
6.2.2 All but three TIES have been removed.  TIES are currently in 14 A and C and 15 B slots.
6.2.3 DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  The Project is waiting on contractors before repairs may be completed.

6.2.4 Removal of the spare STS occurred on 18 July.  TIES were removed from the north end of PH2 to accommodate the barge.
6.2.5 Due to temperatures at the SMF reaching 70(F, personnel will process fish more often to reduce holding time.
7 HAZMAT, SPILLS AND CLEANUP - Nothing to report.
8 TELETYPES AND OTHER NOTEWORTHY ITEMS. 
8.1 A teletype sent on 28 June requests that Bonneville start summer spill of 75 KCFS during daytime hours and spill to the 120% gas cap at night until further notice.
8.2 A teletype sent on 12 July requests a soft constraint of 75.5’ to 76.5’, and a hard constraint of 75.0’ to 76.5’, on the Bonneville pool from 0600, 17 July to 1800, 20 July.  This is to limit wear and tear on gill nets due to pool fluctuations.
8.3 A teletype sent on 13 July requests a soft forebay constraint of 75.0’ – 76.5’ from 0600 until 1800 everyday from 24-29 July.  This operation is necessary for SDS Lumber to maneuver a barge for rock placement.  Additional teletypes will be issued, as needed, until the work is completed in late August.
JAMES R. MAHAR, P.E.

Operations Manager

1

