CENWP-OP-B                                                                                                                          05 September, 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 35 of 2006, which covers the period from 27 August through 02 September 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 100.2 to 149.8 kcfs.  Daily average project tailwater elevation ranged from 8.8’ to 13.5’ msl.  Daily average powerhouse forebay elevation ranged from 74.9’ to 76.1’ msl.  Daily average river temperature ranged between 69( and 71(F.  Secchi disk measurements averaged 6.0 to 7.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 1.5 to 87.6 kcfs.  Juvenile spill concluded for the season at 2358 on 31 August, adult attraction spill continues.
1.3 Unit Operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 10 remains out of service for turbine rehab.
1.3.4 Unit 11 had a 1% violation on 29 August for STS inspections.

1.3.5 Unit 12 was out of service from 0935 until 1035 on 31 August for gland water leak repairs.
1.3.6 Unit 13 remains out of service for a four year overhaul.

1.3.7 Unit 15 had a 1% violation on 29 August for STS inspections.
1.3.8 Unit 16 was out of service from 1230 until 1440 on 30 August for STS repairs.

1.3.9 Unit 18 had a 1% violation on 29 August for STS inspections.  Unit 18 was out of service from 1053 until 1701 on 31 August for packing adjustment.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed.
2.2 STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.
	Unit
	Date
	Run Hours
	Comments

	11
	8/29
	817
	NA

	12
	8/29
	443
	

	13
	8/29
	511
	

	14
	8/29
	198
	

	15
	8/29
	220
	

	16
	8/29
	81
	Replaced rivets in B-slot screen

	17
	8/29
	198
	

	18
	8/29
	834
	


Table 1.  STS and VBS inspections.

2.3 Dewatering and Fish Salvage.  The following dewatering activities occurred this reporting week.
2.3.1 The B2CC was closed at 1545 on 31 August.  The B2CC will reopen in 2007.  No fish were found.
3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF.  Every other day restriction due to temperatures reaching 70(F
3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA Fisheries- Gilbreath.  Salt water rearing subyearling chinook at the SMF continues.   
3.4 NOAA Fisheries- Jacobson.   Collecting subyearling chinook for growth and survival work.  
3.5 NOAA Fisheries lamprey.  On 29 August, permit numbers were reached and tagging concluded.  Final numbers for the year are: 2050 for NOAA Fish and 350 for U of I.
3.6 PSMFC smolt monitoring.  Adopted FPAC sampling protocols due to water temps reaching 70ºF.  Target sample size was reduced to 100 fish per day and processing every two hours throughout the day.  GBT sampling concluded on 31 August.  12 subyearling chinook were collected for NOAA researchers.  
3.7 PSMFC PIT tag.  Monthly testing of the B2CC detectors June through October.
3.8 USGS lamprey.  Lamprey held in the FERL for tagging evaluation.
3.9 WDFW Fish Counting.  Visual fish counting continues.

3.10 WDFW and ODFW.  Tule counting continues.
4 FISHWAYS 

4.1 Project biologists inspected 27 August through 02 September 2006.
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	8/27-28
	A-branch
	Reading <1.0’>
	Unknown
	
	

	9/1
	B-branch
	Diffusers open
	System in manual
	Operators closed FG3-27
	

	9/2
	Weir 37/38
	Reading <1.0’>
	Unknown
	
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed in the winter of 04/05.

4.2.3 Cascades Island FG6-12 is closed due to a bent shaft.  Repairs can not be made until winter 06/07.  this diffuser is out of criteria when tailwater exceeds 13’
4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  For now, the collection channel is operating within FPP criteria.

4.2.5 DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  A portion of the PLC has been reprogrammed.  TR#06-40863.
4.2.6 DSM2 orifice F2 B-S has separated from the shaft.  The orifice is ready for welding.  TR# 06-50979.
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  
	Date
	WS avg.
	BI avg.
	AFF max
	SMF max

	8/27
	71.1
	70.9
	71.1
	70.3

	8/28
	71.7
	71.4
	71.7
	70.9

	8/29
	71.5
	71.2
	71.5
	70.7

	8/30
	70.6
	70.4
	70.6
	69.6

	8/31
	70.1
	69.9
	70.1
	69.2

	9/1
	69.4
	69.4
	69.5
	68.7

	9/2
	68.9
	68.9
	68.9
	67.9


Table 3.  Bonneville Fishway temperatures.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways.    
4.5.1 Calibration is checked on the weekends.  B-branch tailwater and PH1 south collection channel are out of calibration.
4.5.2 Cascades Island and B-Branch PLCs are in manual.  
4.5.3 Stab plates remain installed in the PH2 FOGs.
4.5.4 Due to temperatures at the AFF reaching 70(F, trapping is limited to every other day.  The modified sampling will continue until temperatures drop to 69.5(F and continue on a downward trend.
4.5.5 Weir 7 has a broken cable.  It will be replaced when the AFF goes OOS for winter maintenance.
4.5.6 WS log boom repaired on 30 August.
4.6 Juvenile Fishways.
4.6.1 DSM1 remains out of service until 15 September.

4.6.2 Due to temperatures at the SMF reaching 70(F or greater, personnel will process fish more often to reduce holding time.  The modified sampling will continue until temperatures drop to 69.5(F and continue on a downward trend.
4.6.3 DSM2 orifice F2 B-S has separated from the shaft.  The orifice is in local and closed.  F2 B-N is open to compensate.
4.6.4 The B2CC closed at 1545 on 31 August.  Flushing water was turned on at 1552 and continued until 1752.
4.6.5 The spill was put on seal at 2358 on 31 August.

4.6.6 The SMF hydrocannons were turned off and winterized at 1143 on 01 September.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Unit 11 will go OOS in early Oct, followed by units 15 and 16.

5.4 SMF Full flow PIT Tag Detectors.  Testing ongoing.
6 HAZMAT, SPILLS AND CLEANUP - Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS. 
7.1 A teletype sent on 28 June requests that Bonneville start summer spill at or above 75 KCFS during daytime hours and spill to the 120% gas cap at night until further notice.
7.2 A teletype sent on 18 August requests Bonneville pool be operated with a hard constraint 75.0 -76.5 feet, soft constraint 75.5 – 76.5 feet  to reduce wear and tear on tribal nets during the following times:

7.2.1  0600 on 21 AUG - 1800 on 24 AUG

7.2.2  0600 on 28 AUG - 1800 on 1 SEP

7.2.3  0600 on 5 SEP - 1800 on 9 SEP
7.3 A teletype sent on 28 August requests outflows from BON and TDA remain as low as possible (not to exceed 150 KCFS) from 0700 until 1130 on 04 September.  This request is to reduce currents in the river during the Columbia River Cross Channel Swim at Hood River.
7.4 A teletype sent on 30 August details the rehab testing of Unit 8.  
JAMES R. MAHAR, P.E.

Operations Manager

1

