CENWP-OP-B                                                                                                                 10 September, 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 36 of 2006, which covers the period from 03 through 09 September 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 87.1 to 106.4 kcfs.  Daily average project tailwater elevation ranged from 9.0’ to 10.2’ msl.  Daily average powerhouse forebay elevation ranged from 73.6’ to 76.5’ msl.  Daily average river temperature ranged between 69( and 70(F.  Secchi disk measurements averaged 6.5 to 7.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 1.4 to 1.5 kcfs.  
1.3 Unit Operation.

1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 3 went out of service at 0727 on 06 September for repacking.
1.3.4 Unit 10 remains out of service for turbine rehab.

1.3.5 Unit 13 remains out of service for a four year overhaul.

1.3.6 Unit 14 had a 1% violation and was out of service from 1409 until 1431 on 05 September for reactivity testing.

1.3.7 Unit 15 had a 1% violation and was out of service from 1448 until 1652 on 05 September for reactivity testing.

1.3.8 Unit 16 had a 1% violation and was out of service from 1035 until 1212 on 05 September for reactivity testing.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed for cleaning.
2.1.1 FV1-1 from 0841 until 0901 on 07 September.

2.2 STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.
	Unit
	Date
	Run Hours
	Comments

	11-18
	NA
	NA
	NA


Table 1.  STS and VBS inspections.

2.3 Dewatering and Fish Salvage.  The following dewatering activities occurred this reporting week.
2.3.1 Unit 3 draft tube dewatering was attempted.  A drain valve issue prevented fish from being salvaged.  Please see 7.3
3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF.  

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA Fisheries- Gilbreath.  Salt water rearing subyearling chinook at the SMF continues.   
3.4 NOAA Fisheries- Jacobson.  Collecting subyearling chinook for growth and survival work.  
3.5 PSMFC smolt monitoring.  Resumed normal sampling on 07 September.  12 subyearling chinook were collected for NOAA researchers.  Collection for researchers concluded this week.
3.6 PSMFC PIT tag.  Monthly testing of the B2CC detectors June through October.
3.7 USGS lamprey.  Lamprey held in the FERL for tagging evaluation.
3.8 WDFW Fish Counting.  Visual fish counting continues.  Video to be set up in Cascades Is. on 05 October.
3.9 WDFW and ODFW.  Tule counting will continue from 0700 until 1600 through the end of September.
4 FISHWAYS 

4.1 Project biologists inspected 03 through 09 September 2006.
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	9/4, 9/6
	Weirs 37/38
	Reading <1.0>
	Unknown
	
	

	9/5-7
	FG3-3
	Partially open
	Loss of power
	Repaired on 9/7
	

	9/7
	B-Branch
	FG3-27 open
	System in manual
	Operators closed.
	

	9/9
	BI weirs
	Reading <1.0>
	FV3-9 not controlling properly
	See 4.5.6
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed in the winter of 04/05.

4.2.3 Cascades Island FG6-12 is closed due to a bent shaft.  Repairs can not be made until winter 06/07.  this diffuser is out of criteria when tailwater exceeds 13’
4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  For now, the collection channel is operating within FPP criteria.

4.2.5 DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  A portion of the PLC has been reprogrammed.  TR#06-40863.

4.2.6 DSM2 orifice F2 B-S has separated from the shaft.  The orifice is ready for welding.  TR# 06-50979.

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  
	Date
	WS avg.
	BI avg.
	AFF max
	SMF max

	9/3
	69.2
	68.9
	69.2
	68.2

	9/4
	69.8
	69.5
	69.8
	69.0

	9/5
	70.0
	69.7
	70.0
	69.2

	9/6
	70.1
	70.0
	70.1
	69.3

	9/7
	69.9
	69.8
	69.9
	69.1

	9/8
	69.8
	69.7
	69.9
	69.0

	9/9
	69.6
	69.5
	69.6
	68.7


Table 3.  Bonneville Fishway temperatures.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  B-branch tailwater is out of calibration.
4.5.2 Cascades Island and B-Branch PLCs are in manual.  
4.5.3 Stab plates remain installed in the PH2 FOGs.
4.5.4 Due to temperatures remaining at or below 69.5(F on 05 September, sampling protocols returned to normal.

4.5.5 FG3-3 had a loss of power and would not operate at 0710 on 05 September.  The valve was repaired by 07 September.

4.5.6 Weir 7 broken cable repaired on 06 September.  
4.5.7 FV3-9 was in manual from 07 September until 09 September.  BI water elevations are running high.  The electricians will look at the valve on 11 September.

4.6 Juvenile Fishways.
4.6.1 DSM1, with regional concurrence, will remain OOS.  Screens will not be installed on 15 September.

4.6.2 Due to temperatures remaining at or below 69.5(F on 05 September, sampling protocols returned to normal.
4.6.3 DSM2 orifice F2 B-S has separated from the shaft.  The orifice is in local and closed.  F2 B-N is open to compensate.

4.6.4 On 03 September, DSM2 had low elevations due to low forebay.  

4.6.5 Orifice F2 A-N was opened on 0927 due to low DSM2 water elevations.

5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Unit 11 will go OOS in early Oct, followed by units 15 and 16.

5.4 SMF Full flow PIT Tag Detectors.  Testing ongoing.
6 HAZMAT, SPILLS AND CLEANUP - Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS. 
7.1 A teletype sent on 28 June requests that Bonneville start summer spill at or above 75 KCFS during daytime hours and spill to the 120% gas cap at night until further notice.
7.2 A teletype sent on 28 August requests outflows from BON and TDA remain as low as possible (not to exceed 150 KCFS) from 0700 until 1130 on 04 September.  This request is to reduce currents in the river during the Columbia River Cross Channel Swim at Hood River.
7.3 On 06 September, Unit 3 was ready for dewatering and fish salvage.  Due to a drain valve problem, fish could not be salvaged.  On 08 September, it was determined that the valve could not be repaired.  Tail logs will be pulled on the morning of 11 September.

7.4 A teletype sent on 08 September modifies the dates requested for Bonneville pool to be operated with a hard constraint of 75.0 -76.5 feet and a soft constraint of 75.5 – 76.5 feet to reduce wear and tear on tribal nets. 

 
0600 on 5 SEP - 1800 on 9 SEP



0600 on 11 SEP – 1800 on 15 SEP

JAMES R. MAHAR, P.E.

Operations Manager

1

