CENWP-OP-B                                                                                                                          08 October, 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 40 of 2006, which covers the period from 01 through 07 October 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 79.6 to 116.6 kcfs.  Daily average project tailwater elevation ranged from 7.5’ to 10.5’ msl.  Daily average powerhouse forebay elevation ranged from 76.2’ to 76.4’ msl.  Daily average river temperature ranged between 64( and 66(F.  Secchi disk measurements averaged 6.5 to 7.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 1.2 to 1.4 kcfs.  
1.3 Unit Operation.  
1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 8 remains out of service for turbine rehab. 

1.3.4 Unit 10 remains out of service for turbine rehab.
1.3.5 Unit 13 remains out of service for a four year overhaul.
1.3.6 Unit 16 went out of service at 0722 on 02 October for VBS modifications.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.4.1 When tailwater elevations are very low, only one fish unit is needed to maintain FPP criteria.
1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.   No AWS valves were closed.
2.2 STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.
	Unit
	Date
	Run Hours
	Comments

	11-18
	NA
	NA
	NA


Table 1.  STS and VBS inspections.

2.3 Dewatering and Fish Salvage.  
2.3.1 Biologists removed six sturgeon and seven catfish from Unit 16 draft tube on 04 October. 
3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF.  

3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA Fisheries- Gilbreath.  Fish continue to be held.
3.4 PSMFC smolt monitoring.  50 juvenile shad collected for UI.
3.5 University of Idaho.  Collecting juvenile shad from the SMF to understand their migration biology.  50 juvenile shad received from PSMFC.
3.6 USGS lamprey.  Lamprey held in the FERL for tagging evaluation.
3.7 WDFW Fish Counting.  Visual fish counting continues.

4 FISHWAYS 

4.1 Project biologists inspected 01 through 07 October 2006. 
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	3 Oct
	A-Branch
	FG3-3 stuck
	Unknown
	
	07-2660

	4, 6-7 Oct
	A-Branch 
	Weir reading <1.0
	Unknown
	No action taken
	

	1, 3-4, 7 Oct
	B-Branch 
	Weir reading <1.0
	Unknown
	No action taken
	

	3 Oct
	B-Branch 
	Differential <1.0’
	PLC in manual
	Operators adjusted
	

	4-6 Oct
	B-branch South gate
	Incorrect position for TW elev
	PLC in manual
	Operators adjusted.
	

	4-6 Oct
	Cascades Is. North gate
	Incorrect position for TW elev
	PLC in manual
	Operators adjusted.
	

	5 Oct
	Weirs 37/38
	Reading >1.0’
	UMT closed
	Valve #2 closed.
	

	7 Oct
	Weirs 37/38
	Reading <1.0’
	Valve #2 closed
	Valve #2 opened to 50%
	

	5-7 Oct
	Weir 67
	Reading >1.0’
	UMT closed
	No action taken.
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed.  Will be corrected this winter.
4.2.3 Cascades Island FG6-12 is closed due to a bent shaft.  This is OOC when TW exceeds 13’.  Repairs will be made this winter.  
4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  

4.2.5 DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  A portion of the PLC has been reprogrammed.  TR#06-40863.
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.   
	Date
	Washington Shore average
	Bradford Island average

	10/01
	65.8
	65.8

	10/02
	65.2
	65.2

	10/03
	64.7
	64.6

	10/04
	64.3
	64.1

	10/05
	64.0
	64.0

	10/06
	63.8
	63.5

	10/07
	63.3
	63.0


Table 3.  Bonneville Fishway temperatures.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  Cascades Island entrance is significantly out of calibration.
4.5.2 Cascades Island and B-Branch PLCs are in manual.  
4.5.3 Stab plates remain installed in the PH2 FOGs.
4.5.4 Cascades Island exit was opened at 0900 on 05 October.
4.5.5 The UMT north bulkhead was installed at 0900 on 05 October.  
4.5.6 Due to the UMT closure, Weir 67 is reading greater than 1.0’ +/- .1’.  With FV6-9 completely closed, the only other way to lower the elevation is it to throttle the exit, which Project Fisheries is disinclined to do.  As such, the Weir 67 read 1.2’ – 1.3’ until 01 December.

4.5.7 Due to the UMT closure, Weir 37 and Weir 38 read greater than 1.0’ +/- .1’.  To lower the elevation, Valve #2 (in the AFF) was closed at 1503 on 06 October.  Full closure resulted in elevations less than 1.0’.  At 1203 on 07 October, Valve #2 was open to 50%.  The weirs have remained in criteria.

4.6 Juvenile Fishways.
4.6.1 DSM1 will continue to remain OOS until removal in winter 07/08.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Unit 16 will go OOS in early Oct, followed by units 11 and 15.

6 HAZMAT, SPILLS AND CLEANUP – nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS. 
7.1 A teletype sent on 21 September modifies the dates requested for Bonneville pool be operated with a hard constraint 75.0 -76.5 feet, soft constraint 75.5 – 76.5 feet to reduce wear and tear on tribal nets. 




0600 on 03 OCT – 1800 on 06 OCT

7.2 UMT fish salvage activities will occur on 10 October, just after lunch.
7.3 Bonneville’s winter maintenance schedule is available.  Please contact Fisheries for a copy.
JAMES R. MAHAR, P.E.

Operations Manager

1

