CENWP-OP-B                                                                                                                          22 October, 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 42 of 2006, which covers the period from 15 through 22 October 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 83.0 to 109.5 Kcfs.  Daily average project tailwater elevation ranged from 7.7’ to 9.8’ msl.  Daily average powerhouse forebay elevation ranged from 72.7’ to 76.3’ msl.  Daily average river temperature ranged between 61( and 63(F.  Secchi disk measurements averaged 7.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill averaged 1.2 kcfs.  
1.3 Unit Operation.  
1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 8 remains out of service for turbine rehab. 
1.3.4 Unit 10 remains out of service for turbine rehab.
1.3.5 Unit 11 went out of service at 1519 on 19 October due to a failed STS motor. 

1.3.6 Unit 13 remains out of service for a four year overhaul.
1.3.7 Unit 16 remains out of service for VBS modifications.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 
1.4.1 F2 was on standby from 0035 on 18 October until 1200 on 21 October due to low tailwater.  F2 went out of service at 1200 on 21 October due to an exciter problem.
1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.   The following AWS valves were closed.
2.1.1 FV1-1 was closed for cleaning from 1122 until 1150 on 17 October.
2.2 STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.
	Unit
	Date
	Run Hours
	Comments

	11-18
	NA
	NA
	NA


Table 1.  STS and VBS inspections.

2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage this week.
3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF until late October.
3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA Fisheries- Gilbreath.  Fish continue to be held.
3.4 PSMFC smolt monitoring.  Two steelhead and two salmon were observed crossing the separator bars.  40 juvenile shad collected for UI.
3.5 University of Idaho.  Collecting juvenile shad from the SMF to understand their migration biology.  40 juvenile shad received from PSMFC.
3.6 USGS lamprey.  Lamprey held in the FERL for tagging evaluation.
3.7 WDFW Fish Counting.  Visual fish counting continues at WS and BI.  Video counting at CI.
4 FISHWAYS 

4.1 Project biologists inspected 15-18, 20-21 October 2006.  
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	Weir 67
	Reading >1.0’
	UMT closed
	See 4.5.6
	

	All week
	A-Branch
	FG3-3 stuck
	Unknown
	Will not move.
	07-2660

	10/15, 10/20
	CI differential
	>1.5’
	System in manual
	Operators adjusted
	

	10/16
	BI, A&B branch weirs
	Reading <1.0’
	Dropping FB
	Operators adjusted
	

	10/16-17
	Weir 38
	Reading <1.0’
	Dropping FB
	
	

	10/17-18, 20
	B-Branch
	Diff <1.5’>
	System in manual
	Operators adjusted
	

	10/17
	B-Branch 
	N entrance gate
	System in manual
	Operators opened 
	

	10/17
	Weir 37
	Reading <1.0’
	Unknown 
	Operators adjusted.
	

	10/19
	Inspection
	Not completed
	Staff shortage
	
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed.  Will be corrected this winter.
4.2.3 Cascades Island FG6-12 is closed due to a bent shaft.  This is OOC when TW exceeds 13’.  Repairs will be made this winter.  
4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  

4.2.5 DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  A portion of the PLC has been reprogrammed.  TR#06-40863.
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.   
	Date
	WS average
	BI average

	10/15
	62.9
	62.7

	10/16
	62.4
	62.4

	10/17
	62.4
	61.9

	10/18
	62.2
	61.6

	10/19
	61.8
	61.5

	10/20
	61.3
	61.1

	10/21
	60.8
	60.5


Table 3.  Bonneville Fishway temperatures.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  Cascades Island entrance is significantly out of calibration.
4.5.2 Cascades Island and B-Branch PLCs are in manual.  
4.5.3 Stab plates remain installed in the PH2 FOGs.
4.5.4 Cascades Island exit remains open.
4.5.5 Due to the UMT closure, Weir 67 is reading greater than 1.0’ +/- .1’.  
4.6 Juvenile Fishways.
4.6.1 DSM1 will continue to remain OOS until removal in winter 07/08.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Unit 16 is OOS.  Units 11 and 15 will follow later this Autumn/Winter.
6 HAZMAT, SPILLS AND CLEANUP – nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS. 
7.1 A teletype sent on 17 October cancels the request for a forebay constraint to facilitate salvage activities at Nichols Boatworks.
JAMES R. MAHAR, P.E.

Operations Manager

1

