CENWP-OP-B                                                                                                                          29 October, 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 43 of 2006, which covers the period from 22 through 28 October 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 88.9 to 108.5 Kcfs.  Daily average project tailwater elevation ranged from 8.3’ to 9.8’ msl.  Daily average powerhouse forebay elevation ranged from 75.6’ to 76.3’ msl.  Daily average river temperature ranged between 59( and 60(F.  Secchi disk measurements averaged 7.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill averaged 1.2 to 1.3 kcfs.  
1.3 Unit Operation.  
1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 8 remains out of service for turbine rehab. 
1.3.4 Unit 10 remains out of service for turbine rehab.
1.3.5 Unit 11 returned to service at 1627 on 23 October.  Unit 11 had a 1% violation due to STS inspections on 24 October. 
1.3.6 Unit 14 had a 1% violation due to STS inspections on 24 October.
1.3.7 Unit 13 remains out of service for a four year overhaul.

1.3.8 Unit 16 remains out of service for VBS modifications.
1.3.9 Unit 18 had a 1% violation due to STS inspections on 25 October.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.4.1 F2 returned to service at 1537 on 23 October.  F2 was on standby on 28 October due to low tailwater.
1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.   No AWS valves were closed this reporting week.
2.2 STS/VBS Inspections.  STSs/VBSs were inspected this reporting week.
	Unit
	Date
	Run Hours
	Comments

	11
	10/24
	556
	

	12
	10/24
	664
	

	13
	
	0
	Out of service

	14
	10/24
	500
	No access to C slot until 01 November.

	15
	10/25
	663
	

	16
	
	0
	Out of service for FGE

	17
	10/25
	647
	

	18
	10/25
	665
	


Table 1.  STS and VBS inspections.

2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage this week.
3 RESEARCH
3.1 CRITFC.  Sampling adult fish in the AFF concluded on 24 October.
3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 NOAA Fisheries- Gilbreath.  Fish continue to be held.
3.4 PSMFC smolt monitoring.  One steelhead and one salmon were observed crossing the separator bars.  50 juvenile shad collected for Univ. of Idaho.
3.5 University of Idaho.  Collected 50 juvenile shad from the SMF to understand their migration biology.  
3.6 USGS lamprey.  Lamprey held in the FERL for tagging evaluation.
3.7 WDFW Fish Counting.  Visual fish counting continues at WS and BI.  Video counting at CI.
4 FISHWAYS 

4.1 Project biologists inspected 22-28 October 2006.  
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	Weir 67
	Reading >1.0’
	UMT closed
	No action taken.
	

	10/22
	FG3-27
	Diffuser open
	System in manual
	Operators adjusted
	

	10/22-24, 27-28
	Weir 37
	Reading >1.0’
	
	
	

	10/21-23
	Fish Unit 2
	OOS
	Exciter problems
	
	

	10/19-23
	Unit 11 STS
	STS motor failure
	Unknown
	Unit OOS until repaired
	

	10/23-24, 27
	Weir 38
	Reading >1.0’
	
	
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed.  Will be corrected this winter.
4.2.3 CI FG6-12 is closed due to a bent shaft.  OOC when TW exceeds 13’.  Will be repaired this winter.  
4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  
4.2.5 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660
4.2.6 DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  TR#06-40863.
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.   
	Date
	WS average
	BI average

	10/22
	60.2
	60.0

	10/23
	60.3
	60.1

	10/24
	60.4
	60.1

	10/25
	59.6
	59.4

	10/26
	59.3
	59.2

	10/27
	59.1
	58.8

	10/28
	59.0
	58.7


Table 3.  Bonneville Fishway temperatures.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  Cascades Island entrance is significantly out of calibration.
4.5.2 Cascades Island and B-Branch PLCs are in manual.  
4.5.3 Stab plates remain installed in the PH2 FOGs.
4.5.4 Cascades Island exit remains open.
4.5.5 Due to the UMT closure, Weir 67 is reading greater than 1.0’ +/- .1’.  
4.6 Juvenile Fishways.
4.6.1 DSM1 will continue to remain OOS until removal in winter 07/08.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Unit 16 is OOS.  Units 11 and 15 will follow later this Autumn/Winter.
6 HAZMAT, SPILLS AND CLEANUP – nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS- nothing to report. 
JAMES R. MAHAR, P.E.

Operations Manager

1

