CENWP-OP-B                                                                                                                          12 November, 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 45 of 2006, which covers the period from 05 November through 11 November 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 112.5 to 212.7 Kcfs.  Daily average project tailwater elevation ranged from 11.2’ to 19.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.1’ to 76.2’ msl.  Daily average river temperature ranged between 54( and 55(F.  Secchi disk measurements averaged .2 to 5.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill averaged 1.1 to 37.0 kcfs.  
1.3 Unit Operation.  
1.3.1 Unit 0 remains out of service due to governor trouble.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 8 remains out of service for turbine rehab. 
1.3.4 Unit 9 was out of service from 1214 until 2143 on 08 November to facilitate the crane load testing of gantry 3.
1.3.5 Unit 10 remains out of service for turbine rehab.
1.3.6 Unit 12 VBSs were cleaned from 1014 until 1059 on 08 November and from 0901 until 1103 on 10 November.
1.3.7 Unit 13 remains out of service for a four year overhaul.
1.3.8 Unit 15 was out of service from 0325 until 0930 on 08 November due to STS amp trouble.
1.3.9 Unit 16 remains out of service for VBS modifications.
1.3.10 Unit 17 VBSs were cleaned from 1334 until 1706 on 08 November.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 
1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting week.
2.1.1 FV1-1- closed for cleaning from 1000 until 1040 on 06 November and from 0750 until 1630 on 11 November.

2.1.2 FV3-7- closed for cleaning from 1325 until 1400 on 11 November.

2.1.3 FV3-9- closed for cleaning from 1325 until 1400 on 11 November.

2.1.4 FV5-9- closed for cleaning from 1105 until 1126 on 10 November.
2.2 STS/VBS Inspections.  STSs/VBSs were inspected this reporting week.
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	NA
	NA


Table 1.  STS and VBS inspections.

2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage this week.
3 RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 NOAA Fisheries- Gilbreath.  Fish continue to be held.  
3.3 USGS lamprey.  Lamprey held in the FERL for tagging evaluation.
3.4 WDFW Fish Counting.  Video counting at all three ladders.
4 FISHWAYS 

4.1 Project biologists inspected 05 through 11 November 2006.
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	11/5-8, 11/10-11
	Weir 37
	Reading >1.0’
	Unknown
	No action taken
	

	11/5
	Weir 38
	Reading >1.0’
	Unknown
	No action taken
	

	11/5
	UMT weir
	Reading <1.0’ 
	Unknown
	No action taken.
	

	11/5
	Cascades Is. entrance gates
	Incorrect position for TW elev.
	System in manual
	Operators adjusted gates.
	

	11/6
	FG3-27
	Incorrect position for TW elev.
	System in manual
	Operators closed.
	

	11/6-7, 11/10
	Weir 67
	Reading >1.0’
	UMT closed
	No action taken
	

	11/7-11
	FG3-5
	Incorrect position for TW elev.
	Mechanical failure
	Operators TR’d
	

	11/8
	FG3-6
	Incorrect position for TW elev.
	Mechanical or electrical failure
	To be repaired in 07/08
	

	11/8-11
	B-branch 
	Reading <1.0’
	Unknown
	No action taken.
	

	11/8-11
	BI weir
	Reading <1.0’
	Unknown 
	No action taken.
	

	11/8-10
	A-branch
	Reading <1.0’
	Unknown 
	No action taken.
	

	11/8-11
	Trashracks
	Need cleaned
	Heavy debris
	Riggers working OT
	

	11/9-11
	FG3-7
	Open
	See 4.5.6
	Operators closed.
	

	11/11
	PH1 PCC 
	Low differential
	FV1-1 closed for cleaning.
	System back in criteria at 1630.
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.
4.2.2 PH2 electronic velocity meter was incorrectly installed.  Will be corrected this winter.
4.2.3 CI FG6-12 is closed due to a bent shaft.  OOC when TW exceeds 13’.  Will be repaired this winter.  
4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  
4.2.5 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660
4.2.6 DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  TR#06-40863.
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.   
	Date
	WS average
	BI average

	11/05
	55.3
	55.0

	11/06
	55.9
	55.6

	11/07
	55.9
	55.7

	11/08
	55.1
	55.1

	11/09
	55.0
	54.9

	11/10
	55.1
	54.9

	11/11
	54.2
	54.0


Table 3.  Bonneville Fishway temperatures.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  Cascades Island entrance is significantly out of calibration.
4.5.2 Cascades Island and B-Branch PLCs are in manual.  
4.5.3 Stab plates remain installed in the PH2 FOGs.
4.5.4 Cascades Island exit remains open.
4.5.5 Due to the UMT closure, Weir 67 is reading greater than 1.0’ +/- .1’.  
4.5.6 FG3-3, FG3-5 and FG3-6 are out of service.  FG3-7 was opened to compensate, but created high velocities and flows in the ladder.  Due to the appearance of unfavorable ladder conditions, operators were requested to close FG3-7 until tailwater rises.

4.6 Juvenile Fishways.
4.6.1 DSM1 will continue to remain OOS until removal in winter 07/08.
4.6.2 There is an adult salmonid in DSM2 Add-in channel.  The screen and add-in bars are in proper position.  Biologists will attempt rescue whenever they are on inspection and able to see the fish.

4.6.3 F2 north orifices were closed at 1220 on 06 November and reopened at 0645 on 08 November.
4.6.4 VBSs were cleaned in Unit 12 from 1014 until 1059 on 08 November and from 0901 until 1103 on 10 November.  Unit 17 VBSs were cleaned from 1334 until 1706 on 08 November.

5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Unit 16 is OOS.  Unit 11 will go OOS the first week of December and 15 will follow later.
6 HAZMAT, SPILLS AND CLEANUP – nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype on 05 November requests a hard constraint of a TW at least 11.3’ msl during all hours.  A hard constraint TW 11.3’ – 11.7’ (with a target of 11.5’) between the 0700 until 1900 hours.  Highest TW should occur between 1900 and 0700 hours if flow conditions require.  Tailwater is measured at the gage located on the Oregon side 0.9 miles downstream from Bonneville Dam PH1, 50’ upstream from Tanner Creek and at river mile 144.5.  It is recognized that tidal effects, wind and waves make the operation difficult to implement.  This operation is intended to facilitate chum spawning.  On 02 November, three chum were found while seining below Hamilton Island.  The next survey is on 06 November. 
7.2 A teletype sent on 07 November requests a tailwater increase due to flow conditions.  Effective at 0700 on 07 November, the chum tailwater teletype (see above) is suspended until further notice.  Instead, maintain a tailwater of 13’ or higher.  Provide as many pulses of water as possible, four to six hours in length.  The goal is to create undesirable spawning conditions for chum in the Ives/Hamilton area.  The Project should operate PH1 units outside 1% to minimize VBS and STS debris problems at PH2.  For this operation, PH1 will be the priority powerhouse.  This operation is necessary to accommodate the heavy flows caused by heavy rains.
JAMES R. MAHAR, P.E.

Operations Manager

1

