CENWP-OP-B                                                                                                                          25 November, 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 47 of 2006, which covers the period from 19 November through 24 November 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 109.2 to 135.5 Kcfs.  Daily average project tailwater elevation ranged from 12.1’ to 14.0’ msl.  Daily average powerhouse forebay elevation ranged from 72.9’ to 76.0’ msl.  Daily average river temperature ranged between 50( and 51(F.  Secchi disk measurements averaged 3.0 to 5.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill averaged 1.1 to 1.2 kcfs.  
1.3 Unit Operation.  
1.3.1 Unit 2 remains out of service for turbine rehab.
1.3.2 Unit 5 was out of service from 1855 on 22 November until 1759 on 24 November due to a breaker failure.

1.3.3 Unit 6 was out of service from 1855 on 22 November until 1748 on 24 November due to a breaker failure.

1.3.4 Unit 7 was out of service from 1855 until 2019 on 22 November due to a breaker failure.
1.3.5 Unit 8 remains out of service for turbine rehab. 

1.3.6 Unit 10 remains out of service for turbine rehab.
1.3.7 Unit 11 trashracks were raked from 1308 until 1429 on 21 November and from 1052 until 1145 on 22 November.

1.3.8 Unit 12 VBSs were cleaned from 0852 until 1040 on 22 November.
1.3.9 Unit 13 remains out of service for a four year overhaul.

1.3.10 Unit 16 remains out of service for VBS modifications.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed.
2.1.1 FV1-1- from 1840 on 19 November until 0511 on 20 November to float trash; from 1545 until 1615 on 20 November for cleaning; from 0830 until 0920 on 21 November to facilitate the reattachment of the log boom.
2.1.2 FV3-7- from 1840 on 19 November until 0511 on 20 November to float trash. 
2.1.3 FV3-9- from 1840 on 19 November until 0511 on 20 November to float trash; from 0820 until 0840 on 20 November for cleaning.
2.2 STS/VBS Inspections.  STSs/VBSs were inspected this reporting week.
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	NA
	NA


Table 1.  STS and VBS inspections.

2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage this week.
3 RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 NOAA Fisheries- Gilbreath.  Fish continue to be held.  
3.3 USGS lamprey.  Lamprey held in the FERL for tagging evaluation.
3.4 WDFW Fish Counting.  Video counting at all three ladders.
4 FISHWAYS 

4.1 Project biologists inspected 19 through 24 November 2006.
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	WASHINGTON SHORE

	11/19-20, 11/23-24
	Weir 38
	Reading >1.0’
	Unknown
	No action taken
	

	11/21, 11/23-24
	Weir 37
	Reading >1.1’
	Clogged screen
	Riggers/ops cleaning
	

	11/24
	Weir 67
	Reading >1.0’
	UMT closed
	No action taken
	

	CASCADES ISLAND

	11/21, 11/23-24
	FG6-12
	Incorrect position for TW elev.
	System in manual
	See 4.2.3
	

	11/20, 11/23-24
	Cascades Is
	Head at trashracks
	High debris loads
	Riggers will clean on Monday.
	

	BRADFORD ISLAND AND BRANCHES

	11/19-20
	BI weirs
	Reading <1.0’
	Forebay elevation
	
	

	11/23-24
	BI fishway
	Head at leads, trashracks.
	High debris loads
	Riggers will clean on Monday.
	

	PROJECT WIDE

	11/25
	Bonneville 
	No bio fishway inspection
	Illness
	Operators inspected.
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH2 electronic velocity meter was incorrectly installed.  Will be corrected this winter.
4.2.2 CI FG6-12 is closed due to a bent shaft.  OOC when TW exceeds 13’.  Will be repaired this winter.  
4.2.3 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  

4.2.5 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.   
	Date
	WS average
	BI average

	11/19
	51.7
	51.5

	11/20
	51.6
	51.5

	11/21
	51.8
	51.6

	11/22
	51.8
	51.6

	11/23
	51.5
	51.3

	11/24
	51.2
	51.1

	11/25
	50.9
	50.6


Table 3.  Bonneville Fishway temperatures.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  Cascades Island entrance is significantly out of calibration.
4.5.2 Cascades Island and B-Branch PLCs are in manual.  
4.5.3 Stab plates remain installed in the PH2 FOGs.
4.5.4 Cascades Island exit remains open.
4.5.5 Due to the UMT closure, Weir 67 is reading greater than 1.0’ +/- .1’.  
4.6 Juvenile Fishways.
4.6.1 DSM1 will continue to remain OOS until removal in winter 07/08.
4.6.2 There is an adult salmonid in DSM2 Add-in channel.  The screen and add-in bars are in proper position.  Biologists will attempt rescue whenever they are on inspection and able to see the fish.
4.6.3 Due to a lack of PLC control, DSM2 orifice F1 B-N is in local and open as of 2222 on 22 November.
4.6.4 The B2CC was closed at 1600 on 21 November.

4.7 Lamprey Fishways.

4.7.1 The Bradford Island lamprey ramp was winterized on 21 November.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Unit 16 is OOS.  Unit 11 will go OOS the first week of December and 15 will follow later.
6 HAZMAT, SPILLS AND CLEANUP – nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 17 November requests a hard constraint tailwater elevation minimum of 11.8’ msl during all hours and a hard constraint tailwater elevation of 11.8’ – 12.3’ msl at all hours, but with a priority from 0700 until 1900.  A note in the teletype outlines pulsing operations if needed due to high flows.  This request will remain in effect until after the TMT meeting on 22 November.
7.2 A teletype sent on 20 November outlines tailwater operations for the chum spawning study on 21 November.  It requires ramping flows up, holding the target tailwater for eight hours, then ramping back down.  The teletype requests an increase of tailwater from 12.0’ to 14.0’ msl at 1600 on 21 November and a decrease of tailwater from 14.0’ to 12.0’ msl at 0100 on 22 November.  The Project should attempt to hold the target tailwater within .2’.  At 0100 on 22 November, the Project should return to guidance in the teletype sent on 17 November (see 7.1)
7.3 A teletype sent on 20 November modifies the 17 November teletype (7.1).  This teletype requests two pulses of water at least 20 minutes in length at 1830 on 20 November and 0630 on 21 November.  
7.4 A teletype sent on 22 November replaces the tailwater operation outlined in the 20 November teletype (which modified the 17 November teletype),  see 7.3.  Effective until further notice, but not during any short term chum study operation, a hard tailwater constraint of a minimum 11.8’ during all hours; a hard tailwater constraint of 11.8’ to 12.3’ (targeting 12.0’) during all hours with a priority between 0700 until 1900, except during pulses; at least one pulse of water to last at least 20 minutes and provide at least 13.5’ tailwater.  If there is adequate water to provide two pulses, the teletype requests they occur several hours before dawn and several hours after dusk, if there is only enough water for one pulse, it should occur around midnight.  This operation will be superceeded only by short term chum study operations scheduled by USGS.  The intent of this request is to facilitate chum spawning at lower elevations, yet still keep redds at higher elevations wet.
JAMES R. MAHAR, P.E.

Operations Manager

1

