CENWP-OP-B                                                                                                                          10 December, 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 49 of 2006, which covers the period from 03 through 09 December 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 136.7 to 153.4 Kcfs.  Daily average project tailwater elevation ranged from 12.5’ to 13.6’ msl.  Daily average powerhouse forebay elevation ranged from 72.3’ to 73.6’ msl.  Daily average river temperature ranged between 44( and 46(F.  Secchi disk measurements averaged 3.0 to 6.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill averaged 0.5 to 1.2 kcfs.  
1.2.1 Spill Bay 1 was closed on 09 December due to Cascades Island fishway going to orifice flow.

1.3 Unit Operation.  
1.3.1 Unit 0 was out of service from 2112 on 03 December until 1500 on 04 December due to a loss of governor pressure.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 8 remains out of service for turbine rehab. 

1.3.4 Unit 10 remains out of service for turbine rehab.

1.3.5 Unit 11 went out of service at 0705 on 05 December.
1.3.6 Unit 13 remains out of service for a four year overhaul.

1.3.7 Unit 16 returned to service at 1422 on 04 December.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.4.1 Fish Unit 1 went out of service at 0047 on 09 December to facilitate Washington Shore ladder going to orifice flow.

1.4.2 Fish Unit 2 went out of service at 0056 on 09 December to facilitate the Washington Shore fish ladder going to orifice flow.

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed.
2.2 STS/VBS Inspections.  STSs/VBSs were inspected this reporting week.
	Unit
	Date
	Run Hours
	Comments

	11-18
	NA
	NA
	NA


Table 1.  STS and VBS inspections.

2.3 Dewatering and Fish Salvage.  The following dewatering or fish salvage activities occurred this week.
2.3.1 Unit 11 was dewatered on 06 December.  No fish were found in the draft tube.

2.3.2 The AFF was dewatered on 09 December.  Biologists removed 12 lamprey, two suckers, one adult steelhead, and six juvenile salmonids.  All were released at the new navlock, in good condition.

3 RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 NOAA Fisheries- Gilbreath.  Fish continue to be held.  
3.3 USGS lamprey.  Lamprey held in the FERL for tagging evaluation.
3.4 WDFW Fish Counting.  Video counting at all three ladders.
4 FISHWAYS 

4.1 Project biologists inspected on 5, 7-9 December 2006.
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	WASHINGTON SHORE- at orifice flow on 12/9

	12/8
	Weir 37
	Reading >1.0’
	Unknown
	No action taken
	

	CASCADES ISLAND- at orifice flow on 12/9

	12/8
	UMT weir
	Reading <1.0’
	Low forebay
	
	

	All week
	FG6-12
	Closed
	Diffuser is broken
	To be repaired in Jan.
	

	BRADFORD ISLAND AND BRANCHES

	All week
	PH1 WG 64
	Submergence incorrect
	Gate keeps tripping.
	Electricians notified.
	

	12/8-9
	BI weir
	Reading <1.0’
	Low forebay
	
	

	12/8-9
	B-Branch weir
	Reading <1.0’
	Low forebay
	
	

	12/8-9
	BI picket leads
	Head > .3’
	
	Riggers to clean on 12/11
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH2 electronic velocity meter was incorrectly installed.  Will be corrected this winter.
4.2.2 CI FG6-12 is closed due to a bent shaft.  OOC when TW exceeds 13’.  Will be repaired this winter.  
4.2.3 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.4 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  

4.2.5 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

4.3 Fishway Temperatures.  Temperatures are only taken 01 March through 30 November.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  Cascades Island entrance is significantly out of calibration.
4.5.2 Cascades Island and B-Branch PLCs are in manual.  
4.5.3 Stab plates remain installed in the PH2 FOGs.
4.5.4 Due to the UMT closure, Weir 67 is reading greater than 1.0’ +/- .1’.  
4.5.5 Cascades Island went to orifice flow at 1022 on 09 December.
4.5.6 WS went to orifice flow at 0945 on 09 December.
4.5.7 The AFF was dewatered on 09 December.

4.6 Juvenile Fishways.
4.6.1 DSM1 will continue to remain OOS until removal in winter 07/08.
4.6.2 There is an adult salmonid in DSM2 Add-in channel.  The screen and add-in bars are in proper position.  Biologists will attempt rescue whenever they are on inspection and able to see the fish.

4.7 Lamprey Fishways.  Currently dewatered.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Unit 16 is complete.  Unit 11 is OOS.  Unit 15 will be last.
6 HAZMAT, SPILLS AND CLEANUP – nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 28 November requests a forebay soft constraint of 71.5’ – 72.5’ from 0700 until 1600 (or as long as possible) on 04 December.  This operation is to facilitate environmental clean up at lower elevations near Hood River.

7.2 A teletype sent on 01 December grants permission to operate Unit 16 in normal priority without fish screens in place.  All fish screens will be pulled starting 18 December.

7.3 A teletype sent on 04 December detailed the chum spawning studies planned for 05 and 07 December.  Tests are scheduled to occur during the evening and will require ramping flows up, holding the target for eight hours then ramping back down.  During testing the tailwater elevations below override the elevations outlined in the teletype sent on 22 November (7.1).  If 16.0’ can not be reached, hold tailwater as high as possible.

05 December 1500- increase from 12.0’ to 14.0’

05 December 1600- increase from 14.0’ to 16.0’

06 December 0100- decrease from 16.0’ to 14.0’

06 December 0200- decrease from  14.0’ to 12.0’

07 December 1500- increase from 12.0’ to 14.0’

07 December 1600- increase from 14.0’ to 16.0’

08 December 0100- decrease from 16.0’ to 14.0’

08 December 0200- decrease from  14.0’ to 12.0’

7.4 Teletypes sent on 05  and 07 December indicated the chum spawning study test were canceled for the evening of 05 December due to a lack of spawning chum and the evening of 07 December due to equipment problems.  No further tests are expected for 2006.
7.5 A teletype sent on 06 December replaces the tailwater guidance for chum spawning in the 22 November teletype.  Effective until further notice, but not during any short term chum study operation, a hard tailwater constraint of a minimum 12.3’ during all hours; a hard tailwater constraint of 12.3’ to 12.8’ (targeting 12.5’) during all hours with a priority between 0700 until 1900, except during pulses; at least one pulse of water to last at least 20 minutes and provide at least 13.5’ tailwater.  If there is adequate water to provide two pulses, the teletype requests they occur several hours before dawn and several hours after dusk, if there is only enough water for one pulse, it should occur around midnight.  This operation will be superseded only by short term chum study operations scheduled by USGS.  The intent of this request is to facilitate chum spawning at lower elevations, yet still keep redds at higher elevations wet.  

JAMES R. MAHAR, P.E.

Operations Manager

1

