CENWP-OP-B                                                                                                                          26 December, 2006
MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 51 of 2006, which covers the period from 17 through 23 December 2006.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 112.0 to 171.9 kcfs.  Daily average project tailwater elevation ranged from 13.5’ to 15.7’ msl.  Daily average powerhouse forebay elevation ranged from 73.1’ to 74.7’ msl.  Daily average river temperature ranged between 41( and 42(F.  Secchi disk measurements averaged 3.0 to 6.0 feet.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill averaged 0.5 to 19.2 kcfs.  
1.2.1 Spill Bay 1 remains closed during all hours.
1.3 Unit Operation.  
1.3.1 Unit 0 was out of service from 1417 on 15 December until 1643 on 21 December due to a loss of gate reference.

1.3.2 Unit 2 remains out of service for turbine rehab.
1.3.3 Unit 8 remains out of service for turbine rehab. 
1.3.4 Unit 10 remains out of service for turbine rehab.
1.3.5 Unit 11 remains out of service for VBS mods.
1.3.6 Unit 12 was out of service from 0649 until 1057 on 18 December during STS removal.

1.3.7 Unit 13 remains out of service for a four year overhaul.
1.3.8 Unit 14 was out of service from 0700 until 1030 on 19 December during STS removal.
1.3.9 Unit 15 was out of service from 1029 until 1323 on 19 December during STS removal. 

1.3.10 Unit 17 was out of service from 1106 until 1444 on 18 December during STS removal.
1.3.11 Unit 18 was out of service from 1329 until 1536 on 19 December during STS removal.  
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are currently out of service for winter maintenance. 

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed.
2.1.1 FV1-1 was closed from 1518 until 1530 on 21 December for trashrack cleaning.
2.1.2 FV3-7 was closed from 1008 until 1145 on 18 December for trashrack cleaning. 
2.1.3 FV3-9 was closed from 1008 until 1145 on 18 December for trashrack cleaning.
2.1.4 FV5-3, FV5-4, and FV5-9 remain closed for winter maintenance in the Cascades Island fishway.

2.1.5 FV6-9 remains closed for winter maintenance in the Washington Shore fishway.

2.2 STS/VBS Inspections.  STSs/VBSs were inspected this reporting week.  STSs were removed after inspection.
	Unit
	Date
	Run Hours
	Comments

	11
	12/05
	142
	Removed for VBS mods.  B and C slot screens in poor condition.

	12
	12/18
	423
	

	13
	8/29
	
	Removed for rewedge.

	14
	12/19
	412
	

	15
	12/19
	471
	

	16
	10/02
	
	Removed for VBS mods.  Never reinstalled.

	17
	12/18
	591
	

	18
	12/19
	478
	


Table 1.  STS and VBS inspections.

2.3 Dewatering and Fish Salvage.  The following dewatering or fish salvage activities occurred this week.
2.3.1 The PH2 DSM2 was dewatered on 20 December.  
3 RESEARCH
3.1 ERDC TDG.  Sensors remain installed in the tailrace.

3.2 USGS lamprey.  Lamprey held in the FERL for tagging evaluation.
3.3 WDFW Fish Counting.  Video counting continues at Bradford Island.
4 FISHWAYS 

4.1 Project biologists inspected on 17, 18, 19, 21, December 2006.
4.2  Fish Passage Plan Observations.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES

	12/17-18
	BI trashracks
	Trashracks have high drawdown.
	Debris stuck in the trashracks
	Requested the riggers clean ASAP
	

	12/17-18
	BI picket leads
	Head >.3’
	Debris
	Riggers to clean ASAP
	

	12/17-18
	BI weir
	Reading <1.0’
	Debris
	Riggers to clean
	

	12/17-18
	A branch
	Reading <1.0’
	Debris
	Riggers to clean
	

	12/17-18
	B branch
	Reading <1.0’
	Debris
	Riggers to clean
	


Table 2.  FPP Out of Criteria items.

4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.2 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  

4.2.3 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  
4.5.2 B-Branch PLC is in manual.  
4.5.3 WS and CI remain dewatered.
4.6 Juvenile Fishways.
4.6.1 DSM1 will continue to remain OOS until removal in winter 07/08.
4.6.2 DSM2 screen cleaner #1 is in local control due to mechanical binding.
4.6.3 DSM2 went out of service at 1000 on 20 December.

4.6.4 B2 Corner Collector was open at 0930 on 21 December to flush debris.  Scheduled to be closed at 0900 on 26 December. 
4.7 Lamprey Fishways.  Remains dewatered.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Unit 16 is complete.  Unit 11 is OOS.  Unit 15 will be next.
6 HAZMAT, SPILLS AND CLEANUP – nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 01 December grants permission to operate Unit 16 in normal priority without fish screens in place.  All fish screens will be pulled starting 18 December.

7.2 A teletype sent on 12 December requests a special forebay operation for 18 December.  Forebay elevation will have a hard constraint of 74.5’ msl from 1500 - 1600 on 18 December.  This is to facilitate floating a heavy load barge from Hood River.

7.3 Starting on 14 December, a series of teletypes allow the Project to exceed chum tailwater restrictions due to high flows.  This exceedance has been approved by Jim Mahar and is effective until 18 December.  The Project is requested to maintain as steady an outflow as possible and return to normal operation once control of the lower river has been regained.
7.4 A teletype sent on 20 December updates the targeted tailwater guidance for chum spawning in the 17 December teletype.  Effective until further notice a hard tailwater constraint of a minimum 12.8’ during all hours; a hard tailwater constraint of 12.8’ to 13.3’ (targeting 13.0’) during all hours with a priority between 0700 until 1900, except during pulses; at least one pulse of water to last at least 20 minutes and provide at least 13.5’ tailwater.  If there is adequate water to provide two pulses, the teletype requests they occur several hours before dawn and several hours after dusk, if there is only enough water for one pulse, it should occur around midnight.  This operation will be superseded only by short term chum study operations scheduled by USGS.  The intent of this request is to facilitate chum spawning at lower elevations, yet still keep redds at higher elevations wet.  
7.5 A teletype sent on 22 December replaces the 20 December teletype.   The new tailwater operation is for chum incubation.   Effective as soon as possible, a hard tailwater constraint to operate project tailwater no lower than 13.0 feet during all hours.  One pulse per day with a minimum duration of 20 minutes and minimum elevation of 13.5 feet.  
JAMES R. MAHAR, P.E.

Operations Manager
1

