CENWP-OP-B                                                                                                                          05 March 2007
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 09 of 2007, which covers the period from 25 February through 03 March 2007.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 133.1 to 185.5 kcfs.  Daily average project tailwater elevation ranged from 13.1’ to 16.0’ msl.  Daily average powerhouse forebay elevation ranged from 74.4’ to 75.8’ msl.  Daily average river temperature ranged between 40(F and 41(F.  Secchi disk measurements averaged 5.0’ to 7.0’.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill averaged 0.6 to 0.7 kcfs.  
1.2.1 Spill Bay 1 remains closed during all hours.  

1.2.2 Spill Bay 18 is open during daylight hours.
1.3 Unit Operation. Powerhouse 2 priority.
1.3.1 Unit 2 remains out of service for turbine rehab.
1.3.2 Unit 8 remains out of service for turbine rehab. 

1.3.3 Unit 10 remains out of service for turbine rehab.
1.3.4 Unit 11 was out of service from 0737 until 1526 on 28 February for STS installation.

1.3.5 Unit 13 remains out of service for a four year overhaul.

1.3.6 Unit 15 remains out of service, as of 08 February, to facilitate VBS/gatewell modifications.  
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.4.1 F1 was in reserve standby from 0750 until 1200 on 26 February to facilitate a ROV inspection.  
1.4.2 F2 was in reserve standby from 0800 until 1202 on 26 February to facilitate a ROV inspection.  
1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves are closed.
2.1.1 FV5-3, FV5-4, and FV5-9 remain closed for winter maintenance in the Cascades Island fishway.

2.1.2 FV6-9 remains closed due to the UMT remaining OOS for VBS modification.
2.2 STS/VBS Inspections. No STSs/VBSs were inspected this reporting week.   
Table 1.  STS and VBS inspections.

	Unit
	Date
	Run Hours
	Comments

	11
	2/28
	
	Screens installed

	12
	2/21
	
	Screens installed

	13
	
	
	Currently out of service

	14
	2/22
	
	Screens installed

	15
	
	
	Currently out of service for gatewell mods.

	16
	2/22
	
	Screens installed

	17
	2/21
	
	Screens installed

	18
	2/21
	
	Screens installed.


2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.
3 RESEARCH
3.1 Battelle.  Monitoring with hydroacoustics near B2CC entrance to study kelt passage.  
3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 Fish Field Unit.  Sea lion observations continue.

3.4 NOAA Lamprey.  Construction of the lamprey ramp in the WA shore AWS began in mid January.
3.5 PSMFC Smolt Monitoring.  Index and condition sampling began on 01 March.

3.6 USGS.  Lamprey held in the FERL for tagging evaluation.
3.7 USDA Wildlife Services.  Hazing sea lions from the powerhouses began 01 March. 

3.8 WDFW Fish Counting.  Video counting continues at Bradford Island.  Video counting at WA shore began 21 February.
3.9 WDFW Sea lion hazing.  Hazing from boats began 01 March.
4 FISHWAYS 

4.1 Project biologists inspected 26 February and 01 – 03 March 2007.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES

	2/26
	A-Branch weir
	Staff gage < 1.0
	ROV inspection
	All valves in auto by 1645
	

	2/26
	B-Branch weir 
	Staff gage < 1.0
	ROV inspection
	All valves in auto by 1645
	

	2/26
	BI weir
	Staff gage <1.0
	ROV inspection
	All valves in auto by 1645
	

	3/1-3/3
	PH1 Ice and Trash sluiceway
	Chain gates 1C, 3C, 6C not open
	
	1B, 2B, 3B, and 5A are open at 71.5 msl.
	Riggers notified 

	3/1-3/3
	A-branch
	FG 3-4
	Diffuser not controlling properly
	Operators notified.  TR’d Jan 31st
	

	3/1
	B-Branch 
	Differential < 1.0
	Unknown
	Operators adjusted
	

	3/2
	Weir 37
	Staff gage < 1.0
	Unknown
	Operators adjusted
	

	3/2
	BI exit 
	Trashrack needs to be cleaned
	Wood debris
	Fisheries and operators cleaned 03 March
	


4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.2 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  

4.2.3 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. 
Table 3.  Bonneville Fishway temperatures.
	Date
	WS average
	BI average

	3/1
	41.0
	41.1

	3/2
	41.0
	41.1

	3/3
	41.0
	41.5


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  
4.5.2 B-Branch PLC is partially in auto and manual.  
4.5.3 Washington shore returned to service on 22 February.  Powerhouse priority shifted from PH1 to PH2.   
4.5.4 Cascades Island remains out of service.

4.5.5 SLEDS are installed at PH1, PH2, and B-branch fishway entrances.  

4.6 Juvenile Fishways.
4.6.1 DSM1 continues to remain OOS.
4.6.2 B2 Corner Collector was opened for the season at 1328 on 01 March. 
4.6.3 DSM2 air burst system and brush screen cleaners are in auto.
4.7 Lamprey Fishways.  Remain dewatered.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 24 PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Units 11 and 16 are complete.  Unit 15 is currently OOS.
6 HAZMAT, SPILLS AND CLEANUP – nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 22 December details tailwater operations for chum incubation.   Effective as soon as possible, a hard tailwater constraint to operate project tailwater no lower than 13.0 feet during all hours.  One pulse per day with a minimum duration of 20 minutes and minimum elevation of 13.5 feet. 
7.2 A teletype sent on 26 February requests special tailwater operations for piezometer installation at Ives Island.  Request that Bonneville maintain a 12.0 foot tailwater as a hard constraint for a maximum of four hours effective 1200 to 1600 hours on Wednesday, 28 February.  This is a four hour departure from the current 13.0 feet minimum tailwater operation to protect chum salmon.
7.3 A teletype sent on 01 March details B2 Corner Collector operations.  Effective at approximately 1400, Thursday, 01 March, and lasting until further notice, the project will begin the operation of the B2 Corner Collector.  On 05 March, the Spring Creek National Fish hatchery will release 7.5 million juvenile tule fall chinook.  Following the hatchery release, additional testing will be ongoing in the river that will require the operation of the B2 Corner Collector.  
JAMES R. MAHAR, P.E.

Operations Manager

1

