CENWP-OP-B                                                                                                                          26 March 2007
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 12 of 2007, which covers the period from 18 through 24 March 2007.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 184.5 to 270.1 kcfs.  Daily average project tailwater elevation ranged from 21.2’ to 17.1’ msl.  Daily average powerhouse forebay elevation ranged from 72.4’ to 75.7’ msl.  Daily average river temperature ranged between 44(F and 46(F.  Secchi disk measurements averaged 2.5’ to 5.0’.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 0.5’ during daylight hours and are included in the spill pattern.  Daily average spill averaged 1.3 to 34.7 kcfs.  
1.3 Unit Operation. Powerhouse 2 priority.
1.3.1 Unit 8 remains out of service for turbine rehab. 

1.3.2 Unit 10 remains out of service for turbine rehab.
1.3.3 Unit 13 remains out of service for a four year overhaul.

1.3.4 Unit 15 remains out of service, as of 08 February, to facilitate VBS/gatewell modifications.  
1.3.5 Unit 17 was out of service from 1159 on 18 March until 1008 on 19 March for STS replacement and packing adjustment.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 

1.4.1 F1 was in standby from 1218 until 1644 on 23 March to facilitate the staff gauge replacement activities in the PH2 monoliths.

1.4.2 F2 was in standby from 1232 until 1644 on 23 March to facilitate the staff gauge replacement activities in the PH2 monoliths.

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves are closed.
2.1.1 FV1-1 closed for cleaning from 1603 until 1641 on 19 March.
2.1.2 FV3-7 was closed for cleaning from 1452 until 1603 on 19 March.

2.2 STS/VBS Inspections. No STSs/VBSs were inspected this reporting week.   
Table 1.  STS and VBS inspections.

	Unit
	Date
	Run Hours
	Comments

	11-18
	NA
	NA
	Inspections scheduled for the week of 25 March.


2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities this reporting week.
3 RESEARCH
3.1 Battelle.  Monitoring with hydroacoustics near B2CC entrance to study kelt passage.  
3.2 ERDC TDG.  Sensors remain installed in the tailrace.

3.3 Fish Field Unit.  Sea lion observations continue.

3.4 NOAA Lamprey.  Construction of the lamprey ramp in the WA shore AWS began in mid January.
3.5 PSMFC Smolt Monitoring.  Two adult steelhead crossed the separator bars; sampling continues.
3.6 USGS.  Lamprey held in the FERL for tagging evaluation.
3.7 USDA Wildlife Services.  Hazing sea lions from the powerhouses continues. 

3.8 WDFW Fish Counting.  Video counting continues at Bradford Island and WA shore.
3.9 WDFW/ODFW Sea lion hazing.  Hazing from boats continues.
4 FISHWAYS 

4.1 Project biologists inspected on 18 through 24 March 2007.  
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES

	3/19, 3/23
	BI weir
	Reading <1.0’
	Low forebay
	
	

	3/19, 21, 23
	A-Branch weir
	Reading <1.0’
	Low forebay
	
	

	3/19, 3/23
	B-Branch weir
	Reading <1.0’
	Low forebay
	
	

	3/22-23
	B-Branch diff
	Differential >2.0’
	System in auto
	Operators adjusted.
	

	CASCADES ISLAND

	3/18
	Cascades Is.
	FG6-12 incorrect position
	Unknown
	Operators opened.
	

	3/21
	Cascades Is.
	FG6-10 only open ½ way.
	Reached upper limit
	TR’d
	

	3/22
	Cascades Is.
	Differential >2.0’
	System in auto
	Operators adjusted.
	

	WASHINGTON SHORE

	3/19, 3/23
	Weir 37
	Reading >1.0’
	In manual
	Electricians corrected.
	

	3/23
	Weir 38
	Reading >1.0’
	Unknown
	
	


4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.2 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  

4.2.3 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

4.2.4 FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.  

4.2.5 FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.  

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.
Table 3.  Bonneville Fishway temperatures.

	Date
	WS average
	BI average

	3/18
	44.5
	44.5

	3/19
	44.9
	44.9

	3/20
	45.1
	45.0

	3/21
	45.1
	45.0

	3/22
	45.6
	45.6

	3/23
	46.6
	45.7

	3/24
	46.8
	46.9


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration is checked on the weekends.  
4.5.2 B-Branch and Cascades Island PLCs are being worked on.
4.5.3 SLEDS installed at all main fish entrances. 

4.5.4 Stab plates remain installed in the FOGs due to the sea lion barriers not fitting properly.
4.6 Juvenile Fishways.
4.6.1 DSM1 continues to remain OOS.
4.6.2 DSM2 orifice lights continue to be lighted with the halogen bulbs.
4.6.3 The B2CC was closed from 1200 until 1600 on 23 February to facilitate the plunge pool dive.

4.7 Lamprey Fishways.  
4.7.1 The Bradford Island lamprey ramp went into service on 23 March.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Units 11 and 16 are complete.  Unit 15 is currently OOS.
6 HAZMAT, SPILLS AND CLEANUP – nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 22 December details tailwater operations for chum incubation.   Effective as soon as possible, a hard tailwater constraint to operate project tailwater no lower than 13.0 feet during all hours.  One pulse per day with a minimum duration of 20 minutes and minimum elevation of 13.5 feet. 
7.2 A teletype sent on 16 March requests the Project spill, to flush debris, from 0001 until 0031 on 18 March.  All bays should be open one foot, resulting in 41Kcfs of spill.  A minimum tailwater of 15’ msl is also required during the spill.  This request is to flush debris out of the stilling basin prior to the dive activities scheduled to start on 19 March.
7.3 A teletype sent on 19 March restricts sea lion hazing to outside the BRZ from 0700 until 1500 on 20 through 23 March.  This is to keep the hazers from impacting divers in the stilling basin.  This teletype was modified by one sent on 20 March, which extended the spill bay outage until 1800.

7.4 A teletype sent on 20 March approves an exceedance of the normal winter 24 hour tailwater fluctuation limit of 7.0’.  The date for this exceedance was moved around and finally occurred on 23 March.

7.5 A teletype sent on 21 March requests spill bays 1 and 18 be on sill for four hours each on 22 March.  This closure is to occur between 1000 and 1800.  This request was made so the stilling basin survey crew could dive in those bays.

7.6 A teletype sent on 22 March requests the B2CC closure and a hard tailwater contraint of 12’ msl from 1200 until 1600, and a hard tailwater constraint of 13’ msl from 1600 until 1800 on 23 March.  This request is to facilitate the plunge pool dive from 1200 until 1600; Project staff gauge work in the PH2 monoliths; and chum spawning area activities below Bonneville Dam.
7.7 A teletype sent on 24 March approves an exceedance of the normal winter 24 hour tailwater fluctuation limit of 7.0’ from 0000 until 2400 on 24 March.  This exceedance is needed due to high flows in the lower river and to provide reservoir flexibility without being forced to spill.

JAMES R. MAHAR, P.E.

Operations Manager
1

