CENWP-OP-B                                                                                                                          18 June 2007
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 24 of 2007, which covers the period from 10 through 16 June 2007.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 214.7 to 268.5 kcfs.  Daily average project tailwater elevation ranged from 18.0’ to 20.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 75.0’ msl.  Daily average river temperature remained at 62(F.  Secchi disk measurements averaged 3.5’ to 6.0’.
1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 98.0 to 99.6 kcfs.  
1.2.1 At 2247 on 15 June, the spill pattern was changed to 98 kcfs, so as not to exceed 100 kcfs.
1.3 Unit Operation. Powerhouse 2 is the priority powerhouse.  
1.3.1 Unit 5 went out of service at 0721on 11 June for annual maintenance.

1.3.2 Unit 7 has remained out of service for turbine rehab since 04 June 2007.
1.3.3 Unit 8 has remained out of service for turbine rehab since 12 September 2006.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 
1.4.1 F1  and F2 had reduced loading for lamprey passage studies from:

2200 on 10 June until 0400 on 11 June

2200 on 13 June until 0400 on 14 June

2200 on 14 June until 0400 on 15 June

2200 on 16 June until 0400 on 16 June
1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed this week:
2.2 STS/VBS Inspections.  No STS/VBS inspections this week. 
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11-18
	NA
	NA
	NA


2.3 Dewatering and Fish Salvage.  The following dewatering and fish salvage activities occurred this week.
2.3.1 On 12 June, biologists removed three sturgeon, six lamprey and one catfish from U5 draft tube.
3 RESEARCH  
3.1 Battelle spillway survival.  Releasing yearling chinook in the main dam forebay to evaluate survival.
3.2 CTUIR- lamprey.  Will receive AFF trapped lamprey from NOAA researchers for broodstock purposes.
3.3 CTWS- lamprey.  Will receive AFF trapped lamprey from NOAA researchers for ceremonial purposes.
3.4 NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility.

3.5 NOAA- Ferguson.  B2CC detection evaluation underway.  

3.6 NOAA.  Tagging juvenile yearling chinook at the Smolt Monitoring Facility. 

3.7 NOAA Lamprey.  Tagging of lamprey for LPS and UI continue.  
3.8 PSMFC Smolt Monitoring.  One salmon and one steelhead fell back over the separator bars.  One largescale sucker was collected for Bradford Island Remedial Investigations.  320 subyearling chinook were collected for NOAA research.  See: http://www.fpc.org/CurrentDaily/Gbtsum.txt for GBT exam results.
3.9 University of Idaho- lamprey.  Block study for lamprey entrance evaluations at WS began on 01 June.
3.10 University of Idaho- salmon.  Sampling for S. Fork Salmon chinook continues. 
3.11 USACE TDG.  New TDG monitors were installed in the spillway tailrace.

3.12 USDA Wildlife Services.  Avian hazing began on 07 May.
3.13 USGS.  Lamprey will be removed from the FERL on 08 June.
3.14 WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore
4 FISHWAYS 

4.1 Project biologists inspected daily from 10 through 16 June.  
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES

	6/15
	B-branch 
	FG3-23 incorrect
	Unknown
	Electricians working on the diffuser.
	

	6/15-16
	B-branch weir
	Reading <1.3’
	FV3-9 a little low.
	Operators adj. FV3-9
	

	6/15-16
	BI weir
	Reading <1.1’
	FV3-9 a little low
	Operators adj. FV3-9
	

	Once
	Calibration
	Check not done
	KW not yet trained.
	Training scheduled 6/13
	

	CASCADES ISLAND

	6/10-11
	FG6-10
	Closed
	Shaft and motor have parted ways.
	TR submitted.  See 4.2.6
	07-37350

	All week
	FG6-14
	½ way open
	Electricians need to do some rewiring.
	Electricians and riggers working out scheduling.
	

	WASHINGTON SHORE

	All week
	11A-S
	Closed
	Broken shaft
	Mech. working on it.
	07-40917

	All week
	DSM2
	SC #1, #2 in manual
	Broken proximity switch.
	Waiting on electrical parts.
	


4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.2 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  

4.2.3 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

4.2.4 FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.  

4.2.5 FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.  

4.2.6 FG6-10 closed.  Only out of criteria when tailwater is above 19.0’ msl.  Gear box work will begin the week of 11 June.
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.
Table 3.  Bonneville Fishway Temperatures.

	Date
	WS average
	BI average

	6/10
	62.3
	62.1

	6/11
	62.2
	61.7

	6/12
	62.2
	62.0

	6/13
	62.4
	62.2

	6/14
	62.2
	62.1

	6/15
	62.2
	62.1

	6/16
	61.8
	61.4


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration will be checked on weekends.
4.5.2 B-Branch was put into manual on 2 June.  Cascades Island remains in auto.
4.5.3 FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.
4.5.4 Fish ladders remain in shad passage mode.
4.6 Juvenile Fishways.
4.6.1 PH1 chaingates 1A and 1B remain closed at this time.
4.6.2 1C, 3C, and 6C remain set at 70’ msl.
4.6.3 DSM1 remains OOS.
4.6.4 DSM2 were switched back to LEDs on 4 June.
4.7 Lamprey Fishways.  
4.7.1 The Bradford Island lamprey ramp remains in service.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Units 14 and 18 are scheduled for winter 07/08.  U17 VBS monitoring equipment will be installed at this time as well.
6 HAZMAT, SPILLS AND CLEANUP.  Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 06 April requests juvenile spill start at 0001 on 10 April.  Bonneville will spill 100K 24 hours a day.  The spill table may be found in the 1007 FPP page Bon-51, Table Bon-15.  At no time will the project voluntarily spill above the 120% gas cap.

7.2 A teletype sent on 21 May requests that the Washington shore adult ladders be reduced to 0.5 feet head from 2200 until 0400 hours for a lamprey test running from 2 June until 1 October.  
7.3 A teletype sent on 07 June requests that all Lower Snake and Columbia River FCRPS projects operate all turbine units within the 1% best efficiency standard during the best efficiency operating period (April 1 through October 31).  Operation outside of 1% is allowed for maintenance, start up/shut down and other instances as outlined in the Fish Passage Plan.  Operation outside of 1% is NOT allowed for any other reason unless a power emergency has been declared.
7.4 A teletype sent on 14 June requests that Bonneville forebay be operated with a hard constraint of 75.0’ to 76.5’ and a soft constraint of 75.5’ to 76.5’ from 0600 on 18 June until 1800 on 20 June.  This will help reduce wear and tear on tribal gill net equipment.
JAMES R. MAHAR, P.E.

Operations Manager
1

