CENWP-OP-B                                                                                                                          25 June 2007
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 25 of 2007, which covers the period from 17 through 23 June 2007.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 194.4 to 229.4 kcfs.  Daily average project tailwater elevation ranged from 16.3’ to 18.5’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 76.0’ msl.  Daily average river temperature ranged from 61 to 63(F.  Secchi disk measurements averaged 5.0’ to 6.6’.
1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 91.3 to 102.8 kcfs.  
1.3 Unit Operation. Powerhouse 2 is the priority powerhouse.  
1.3.1 Unit 5 has remained out of service for annual maintenance since 11 June.
1.3.2 Unit 7 has remained out of service for turbine rehab since 04 June 2007.
1.3.3 Unit 8 has remained out of service for turbine rehab since 12 September 2006.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 
1.4.1 F1  and F2 had reduced loading for lamprey passage studies from:

2200 on 19 June until 0400 on 20 June

2200 on 20 June until 0400 on 21 June

2200 on 22 June until 0400 on 23 June

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  No AWS valves were closed this week.
2.2 STS/VBS Inspections.  No STS/VBS inspections this week. 
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11-18
	NA
	NA
	NA


2.3 Dewatering and Fish Salvage.  No dewatering and fish salvage activities occurred this week.
3 RESEARCH  
3.1 Battelle spillway survival.  Releasing yearling chinook in the main dam forebay to evaluate survival.
3.2 CRITFC.  Sampling chinook, coho, steelhead and sockeye throughout the season.  Sockeye sampling concluded on 19 June.
3.3 CTUIR- lamprey.  Will receive AFF trapped lamprey from NOAA researchers for broodstock purposes.
3.4 CTWS- lamprey.  Will receive AFF trapped lamprey from NOAA researchers for ceremonial purposes.
3.5 NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility.

3.6 NOAA- Ferguson.  B2CC detection evaluation underway.  

3.7 NOAA- McComas. Tagging juvenile yearling chinook at the Smolt Monitoring Facility. 

3.8 NOAA Lamprey.  Tagging of lamprey for LPS and UI continue.  
3.9 PSMFC Smolt Monitoring.  Three steelhead fell back over the separator bars.  1609 subyearling chinook were collected for NOAA and Battelle research.  See: http://www.fpc.org/CurrentDaily/Gbtsum.txt for GBT exam results.
3.10 University of Idaho- lamprey.  Block study for lamprey entrance evaluations at WS began on 01 June.
3.11 University of Idaho- salmon.  Sampling for S. Fork Salmon chinook continues. 
3.12 University of Idaho-shad.  Sampling for shad continues.

3.13 USACE TDG.  New TDG monitors were installed in the spillway tailrace.

3.14 USDA Wildlife Services.  Avian hazing began on 07 May.
3.15 USGS.  Shad sampling is scheduled to begin 2 July.
3.16 WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore
4 FISHWAYS 

4.1 Project biologists inspected daily from 17 through 23 June.  
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES

	6/23
	B-branch 
	FG3-23 incorrect position for tailwater
	Unknown
	Operator adjusted
	

	6/19
	B-branch weir
	Reading <1.3’
	FV3-9 a little low.
	Operators adj. FV3-9
	

	6/17
	B-branch south gate closed
	Incorrect position for tailwater
	Unknown
	Operator adjusted
	

	6/17
	BI weir
	Reading <1.1’
	FV3-9 a little low
	Operators adj. FV3-9
	

	CASCADES ISLAND

	All week
	FG6-10
	Valve not operational
	Shaft and motor have parted ways.
	TR submitted.  See 4.2.6
	07-37350

	6/17
	Cascades Island entrance
	Differential >2.0
	In manual
	Operator adjusted
	

	6/17
	Cascades Island entrance
	South gate closed
	In manual
	Operator adjusted
	

	All week
	FG6-14
	½ way open
	Electricians need to do some rewiring.
	Electricians and riggers working out scheduling.
	

	WASHINGTON SHORE

	All week
	DSM2
	SC #1, #2 in manual
	Broken proximity switch.
	Waiting on electrical parts.
	


	All week
	DSM2
	Add-in/ orifices
	See 4.6.5
	See 4.6.5
	

	All week
	DSM2
	Screens 6 and 9 not working.
	Bad controls.
	Will replace during winter maintenance.
	Two TRs submitted


4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.2 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  

4.2.3 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

4.2.4 FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.  

4.2.5 FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.  

4.2.6 FG6-10 closed.  Only out of criteria when tailwater is above 19.0’ msl.  Gear box work will begin the week of 11 June.
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.
Table 3.  Bonneville Fishway Temperatures.

	Date
	WS average
	BI average

	6/17
	62.0
	61.7

	6/18
	61.8
	61.7

	6/19
	62.2
	62.1

	6/20
	62.7
	62.8

	6/21
	63.4
	63.4

	6/22
	63.7
	63.6

	6/23
	63.6
	63.5


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 21 June.  All sensors are out of calibration.  A work order was submitted on 22 June.  WO#07-
4.5.2 B-Branch and Cascades Island are in maunal.
4.5.3 FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.
4.5.4 Fish ladders remain in shad passage mode.
4.6 Juvenile Fishways.
4.6.1 PH1 chaingates 1A and 1B remain closed at this time.
4.6.2 1C, 3C, and 6C remain set at 70’ msl.
4.6.3 DSM1 remains OOS.
4.6.4 DSM2 11A-S orifice returned to service on 11 June.  
4.6.5 DSM2 has experienced high water levels this reporting week.  In an effort to keep the ERG from tripping, the Add-in water was reduced to 50% and all regulating orifices were closed.  In addition, the airburst system was set to heavy debris loads with an increase in blow time from 1.5 seconds to 2.0 seconds for all screens.  The dewatering screens do not appear to have debris on them at this time.  The mechanical screens will be returned to service as soon as parts and labor are available.

4.7 Lamprey Fishways.  
4.7.1 The Bradford Island lamprey ramp remains in service.
4.7.2 Washington Shore NDE lamprey ramp was put into service on 29 May.
4.7.3 The Washington shore FV6-9 lamprey ramp was put into service on 18 June.
5 CONSTRUCTION
5.1 B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.
5.2 PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

5.3 PH2 VBS mods.  Units 14 and 18 are scheduled for winter 07/08.  U17 VBS monitoring equipment will be installed at this time as well.
6 HAZMAT, SPILLS AND CLEANUP.  Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 06 April requests juvenile spill start at 0001 on 10 April.  Bonneville will spill 100K 24 hours a day.  The spill table may be found in the 1007 FPP page Bon-51, Table Bon-15.  At no time will the project voluntarily spill above the 120% gas cap.

7.2 A teletype sent on 21 May requests that the Washington shore adult ladders be reduced to 0.5 feet head from 2200 until 0400 hours for a lamprey test running from 2 June until 1 October.  
7.3 A teletype sent on 07 June requests that all Lower Snake and Columbia River FCRPS projects operate all turbine units within the 1% best efficiency standard during the best efficiency operating period (April 1 through October 31).  Operation outside of 1% is allowed for maintenance, start up/shut down and other instances as outlined in the Fish Passage Plan.  Operation outside of 1% is NOT allowed for any other reason unless a power emergency has been declared.
7.4 A teletype sent on 14 June requests that Bonneville forebay be operated with a hard constraint of 75.0’ to 76.5’ and a soft constraint of 75.5’ to 76.5’ from 0600 on 18 June until 1800 on 20 June.  This will help reduce wear and tear on tribal gill net equipment.
7.5 A teletype sent on 19 June requests a soft forebay constraint of 71.5’ – 72.5’ msl from 0900 until 1800 on 23 June and from 0900 until 1200 on 24 June.  This operation is to allow a work party to stockpile debris on the kite board stating area to provide safer kiteboarder conditions.  
7.6 A teletype sent on 20 June details the start of summer spill for juvenile fish passage.  It supercedes the teletype sent on 06 April (see 7.1).  

7.6.1 From 0001 on 21 June until 2400 on 15 July, Bonneville will spill 85K during daytime hours using the spill pattern provided by Dennis Schwartz, labeled “Bonneville Spill Patterns- 50-100kcfs”.  Bonneville will spill to the gas cap at night.  Refer to the 2007 FPP, page BON-14 Table BON-6 for daytime hours.

7.6.2 From 0001 on 16 July until 2400 on 31 August, Bonneville will spill 75K during daytime hours, using the spill pattern provided by Dennis Schwartz, and to the gas cap at night.

7.6.3 If it is necessary to spill above 110kcfs, the Control Room will use the spill pattern found in the 1007 FPP page Bon-51, Table Bon-15.  
7.6.4 At no time will the Project voluntarily spill above the 120% gas cap.  The 120% spill cap level for Bonneville can be found in the teletype “SPILL PRIORITY LIST”. 

7.6.5 At all times, maintain a minimum generation of 30kcfs and minimum spill of 50kcfs.
7.7 A teletype sent on 20 June requests spill bays 2-17 be on seal  from 1200 until NLT 1600 on 24 June.  Bays 1 and 18 will remain open .5’ to maintain adult fishway attraction flows.  This operation is needed to perform a hydrosurvey in the main dam stilling basin.
JAMES R. MAHAR, P.E.

Operations Manager
1

