CENWP-OP-B                                                                                                                         October 1, 2007
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 39 of 2007, which covers the period from 23 September through 29 September 2007.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 73.3 to 94.8 kcfs.  Daily average project tailwater elevation ranged from 7.7’ to 9.0’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 74.3’ msl.  Daily average river temperature ranged from 65( to 66°F.  Secchi disk measurements averaged 7.0’.
1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 1.3 to 1.4 kcfs.   
1.3 Unit Operation. Powerhouse 2 is the priority powerhouse.
1.3.1 Unit 3 went out of service at 0028 on 24 September for the bank ¾ outage.  
1.3.2 Unit 4 went out of service at 0028 on 24 September for the bank ¾ outage.
1.3.3 Unit 7 has remained out of service for turbine rehab since 04 June 2007.

1.3.4 Unit 8 has remained out of service for turbine rehab since 12 September 2006.
1.3.5 Unit 11 was out of service from 0657 until 1110 on 27 September for STS repairs.  
1.3.6 Unit 12 went out of service at 0354 on 17 September for exciter replacement.

1.3.7 Unit 14 has remained out of service since 13 August for re-wedge.

1.3.8 Unit 18 was out of service from 1243 until 1345 on 26 September for STS inspections.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 
1.4.1 F1 and F2 had reduced loading for lamprey passage studies from:

2200 on 22 September until 0357 on 23 September
2200 on 25 September until 0400 on 26 September

2200 on 27 September until 0504 on 28 September

2230 on 28 September until 0411 on 29 September

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  No AWS closures this week.
2.2 STS/VBS Inspections.  The following STS/VBS inspections occurred this week: 

Table 1.  STS and VBS inspections.  

	Unit
	Date
	Run Hours
	Comments

	11
	9/27
	718
	Replaced both belts 11-A slot

	12
	9/27
	424
	

	13
	9/27
	484
	

	14
	
	
	OOS

	15
	9/27
	665
	

	16
	9/27
	194
	

	17
	9/27
	622
	

	18
	9/27
	717
	


2.3 Dewatering and Fish Salvage.  No dewatering and fish salvage activities occurred this week.
3 RESEARCH  
3.1 CRITFC.  Normal sampling operations continue.
3.2 NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility continues.
3.3 PSMFC Smolt Monitoring.  No fallbacks observed crossing the separator bars.  88 juvenile shad were collected for USGS.  
3.4 University of Idaho- lamprey.  Block study for lamprey entrance evaluations will conclude on 01 October.
3.5 USGS shad.  Collected 88 juvenile shad from the SMF.

3.6 WDFW Fish Counting.  Daily visual counting continues at Bradford Island and Washington Shore.  Tule counting continues until 30 September.  
4 FISHWAYS 

4.1 Project biologists inspected daily from 23 September through 30 September.  NOAA inspected on 26 September.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES

	9/29
	B-branch differential
	Reading <1.0>
	System in manual
	Operator adjusted.
	

	CASCADES ISLAND

	All week
	FG6-14
	½ way open
	Electricians need to do some rewiring.
	Winter maintenance item.
	

	WASHINGTON SHORE

	All week
	DSM2 Airburst
	Screens 3, 6 and 9 not consistent.
	Bad controls.
	Will replace during winter maintenance.
	

	All week
	DSM2 PLC
	Not functioning at DSM2
	
	Repairs won’t be made until Dec/Jan
	

	9/27
	PH 2
	Unit 11 priority and orifices 11A-S and 11A-N closed.
	11A STS repairs. 
	Unit 11 and orifices in service by 1110.  
	


4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.2 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  

4.2.3 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

4.2.4 FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.  

4.2.5 FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

4.2.6 FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.  
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.
Table 3.  Bonneville Fishway Temperatures.

	Date
	WS average
	BI average
	AFF average
	JMF average

	9/23
	66.1
	65.8
	66.1
	65.1

	9/24
	65.6
	65.5
	65.6
	64.6

	9/25
	65.7
	65.3
	65.7
	64.8

	9/26
	65.5
	65.1
	65.5
	64.5

	9/27
	65.7
	65.4
	65.7
	64.6

	9/28
	65.3
	65.0
	65.2
	64.3

	9/29
	64.5
	64.3
	64.4
	63.4


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 29 September.  
4.5.2 B-Branch and Cascades Island are in manual.
4.5.3 FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.
4.5.4 DSM1 continues to run south.  All available orifices are open.  U3 orifices were opened at 1030 on 17 September.
4.5.5 The PH2 upstream migration channel is scheduled to close and the Cascades Is. exit to open on 01 October.  
4.6 Juvenile Fishways.
4.6.1 DSM1 is watered up and running south.  See 4.5.4
4.6.2 DSM2 PLC is OOS.  Estimated time of repair is December or January.

4.6.3 11A-N and 11A-S orifices were closed from 0739 until 1038 on 27 September during STS repairs.

4.7 Lamprey Fishways.  
4.7.1 All lamprey passage structures remain in service.
5 CONSTRUCTION
5.1 PH1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

5.2 Bradford Island fish exit dredging.  Sediment sampling and sounding occurred on 31 July.

5.3 Bradford Island clean-up.  Removal of contaminated sediment scheduled to occur in October 2008.  Pre-removal sampling will occur 24 September.

5.4 PH2 VBS mods.  Units 14 and 18 are scheduled for winter 07/08.  U17 VBS monitoring equipment will be installed at this time as well.

6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 21 May requests that the Washington shore adult ladders be reduced to 0.5 feet head from 2200 until 0400 hours for a lamprey test running from 2 June until 1 October.  
7.2 A teletype sent on 07 June requests that all Lower Snake and Columbia River FCRPS projects operate all turbine units within the 1% best efficiency standard during the best efficiency operating period (April 1 through October 31).  Operation outside of 1% is allowed for maintenance, start up/shut down and other instances as outlined in the Fish Passage Plan.  Operation outside of 1% is NOT allowed for any other reason unless a power emergency has been declared.
7.3 A teletype sent on 28 September extends treaty fishing restrictions.  It requests that the Bonneville forebay have a hard constraint of 75.0’ to 76.5’ msl and a soft constraint of 75.5’ to 76.5’ msl from 0600 on 03 October until 1800 on 06 October.  This is to reduce the wear and tear on tribal gill net equipment.  
JAMES R. MAHAR, P.E.

Operations Manager
1

