CENWP-OP-B                                                                                                                         November 5, 2007
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 44 of 2007, which covers the period from 28 October through 03 November 2007.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 85.5 to 107.2 kcfs.  Daily average project tailwater elevation ranged from 8.3’ to 9.8’ msl.  Daily average powerhouse forebay elevation ranged from 74.9’ to 75.5’ msl.  Daily average river temperature ranged from 54° to 56°F.  Secchi disk measurements were 7.0’ every day.
1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 0.6 to 1.3 kcfs.   
1.3 Unit Operation. Powerhouse 2 is the priority powerhouse.
1.3.1 Unit 1 went out of service at 1551 on 23 October due to governor trouble.
1.3.2 Unit 5 was out of service from 0104 until 0127 on 29 October and from 1621 until 1908 on 30 October for switching.

1.3.3 Unit 5 was forced out of service from 1908 on 30 October until 1750 on 1 November due to transformer differential.
1.3.4 Unit 6 was out of service from 0104 until 0127 on 29 October and from 1621 until 1908 on 30 October for switching.

1.3.5 Unit 6 was forced out of service from 1908 on 30 October until 1750 on 1 November due to transformer differential.
1.3.6 Unit 7 has remained out of service since 04 June for turbine rehab.

1.3.7 Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

1.3.8 Unit 11 has remained out of service since 15 October for exciter replacement.
1.3.9 Unit 14 has remained out of service since 13 August for re-wedge and FGE modifications.
1.3.10 Unit 18 was out of service from 1000 until 1055 on 30 October for STS inspection.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris. 
1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting period: 
2.1.1 FV1-1 was closed from 0740 until 0753 on 29 Oct. 

2.2 STS/VBS Inspections.  The following STS/VBS inspections occurred this week: 

Table 1.  STS and VBS inspections.  

	Unit
	Date
	Run Hours
	Comments

	1
	10/26
	189
	Moved STSs to U4 on 26 October.

	3
	10/30
	893
	

	11
	10/30
	444
	

	12
	10/30
	435
	

	13
	10/30
	755
	

	14
	
	
	OOS

	15
	10/30
	797
	

	16
	10/30
	512
	

	17
	10/30
	797
	

	18
	10/30
	798
	


2.3 Dewatering and Fish Salvage.  
2.3.1 Sixteen sturgeon and 1 catfish were removed from Unit 1 draft tube on 31 October.  All were released at the Hamilton Island boat launch in good condition.
3 RESEARCH  
3.1 NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility continues.
3.2 PSMFC Smolt Monitoring.  One salmon and one steelhead were recorded crossing the separator bars this week.  158 juvenile shad collected for researchers.  Smolt monitoring concluded at 0700 on 31 October.
3.3 Univ. of Idaho.  Received 78 juvenile shad from the SMF this week.

3.4 USGS shad.  Received 80 juvenile shad from the SMF this week.
3.5 WDFW Fish Counting.  Daily visual counting concluded at Bradford Island and Washington Shore on 31 October and video counting began on 1 November.  Video monitoring at Cascades Island began on 1 October.
4 FISHWAYS 

4.1 Project biologists inspected daily from 28 October through 03 November. 
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES

	10/29-10/30, 11/3
	B-branch diffusers
	FG 3-27 incorrect position for TW
	System in manual
	Operators adjusted
	

	10/29, 10/31
	B-branch entrance
	N. gate incorrect position for TW
	System in manual
	Operators adjusted
	

	CASCADES ISLAND

	
	CI diff.
	Reading <1.0’>
	System in manual
	Operators adjusted.
	

	10/30
	CI entrance
	N. gate incorrect position for TW
	System in manual
	Operators adjusted.
	

	10/28-10/29
	CI exit 
	Debris on exit trashrack
	
	Riggers to clean
	

	All week
	FG6-14
	½ way open
	Electricians need to do some rewiring.
	Winter maintenance item.
	

	WASHINGTON SHORE

	10/31-11/1
	DSM2
	12A-S closed
	Orifice light research
	Research concluded
	

	All week
	DSM2 Airburst
	Screens 3, 6 and 9 not consistent.
	Bad controls.
	Will replace during winter maintenance.
	


4.2.1 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter often reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.2 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.  

4.2.3 FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

4.2.4 FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.  

4.2.5 FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

4.2.6 FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.
4.3.1 The Bradford Island temperature sensor is malfunctioning and is awaiting repair.
  Table 3.  Bonneville Fishway Temperatures
	Date
	WS average
	BI average

	10/28
	56.8
	See 4.3.1

	10/29
	56.9
	

	10/30
	57.1
	

	10/31
	56.6
	

	11/01
	56.2
	

	11/02
	55.9
	

	11/03
	55.8
	


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 2 November.  
4.5.2 B-Branch and Cascades Island are in manual.
4.5.3 FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.
4.5.4 DSM1 continues to run south.  All available orifices are open.  
4.5.5 The UMT remains closed.  Cascades Island exit remains open. 
4.6 Juvenile Fishways.
4.6.1 DSM2 PLC is OOS.  Estimated time of repair is December or January.

4.6.2 SMF hydrocannons resumed operation on 04 October.  
4.6.3 The SMF was put to bypass at 0700 on 31 October.
4.7 Lamprey Fishways.  Winterized.
5 CONSTRUCTION
5.1 PH1 ITS Wall Removal.  Plans to install three automated gates.  Optional items include sloping the floor and removing the DSM wall.
5.2 Bradford Island clean-up.  Removal of contaminated sediment currently underway.
5.3 PH2 VBS mods.  Unit 14 is currently OOS.  U18 will follow.  U17 VBS monitoring equipment will be installed at this time as well.

5.4 TIE crane.  The TIE crane boom repair is on hold until funding is secured.

6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 07 June requests that all Lower Snake and Columbia River FCRPS projects operate all turbine units within the 1% best efficiency standard during the best efficiency operating period (April 1 through October 31).  Operation outside of 1% is allowed for maintenance, start up/shut down and other instances as outlined in the Fish Passage Plan.  Operation outside of 1% is NOT allowed for any other reason unless a power emergency has been declared.
JAMES R. MAHAR, P.E.

Operations Manager
1

