CENWP-OP-B                                                                                                                         January 3, 2008
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 52 of 2007, which covers the period from 23 December through 29 December 2007.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 120.7 to 171.6 kcfs.  Daily average project tailwater ranged from 13.2’ to 16.3’ msl.  Daily average powerhouse forebay elevation ranged from 74.3’ to 75.6’ msl.  Daily average river temperature ranged from 41° to 43°F.  Secchi disk measurements ranged from 5.0’ to 7.0.’
1.2 Spill Bay 1, which supplies attraction flow for Cascades Island, is included in the spill pattern.  Daily average spill ranged from 0.5 to 0.6 kcfs.
1.3 Unit Operation.   Powerhouse 2 is the priority powerhouse.
1.3.1 Unit 1 has remained out of service since 23 October due to governor trouble.
1.3.2 Unit 5 was out of service on 28 December from 0933 until 1147 due to governor failure.

1.3.3 Unit 7 has remained out of service since 04 June for turbine rehab.

1.3.4 Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

1.3.5 Unit 14 returned to service at 1058 on 22 December.  It had been out of service since 13 August for re-wedge and FGE modifications.  Unit 14 was out of service on 23 December from 1153 until 1434 due to governor cycling and overheating.
1.3.6 Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.
1.3.7 Unit 18 has remained out of service since 03 December for FGE modifications and 4 year overhaul.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 Unit F2 has remained out of service since 03 December for exciter replacement.  
1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting period: 
2.1.1 FV 1-1, 3-7, and 3-9 remain closed for winter maintenance in A-branch.

2.1.2 FV 4-3 and 4-4 remain closed for winter maintenance in B-branch.
2.2 STS/VBS Inspections.  No STS/VBS inspections occurred this week: 
Table 1.  STS and VBS inspections.  

	Unit
	Date
	Run Hours
	Comments

	3-4, 11-18
	NA
	NA
	All screens were pulled for winter maintenance.


2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.
3 RESEARCH  
3.1 WDFW Fish Counting.  Video counting continues at Cascades Island and WA Shore.
4 FISHWAYS 

4.1 Project biologists inspected on 26-28 December.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES- OOS for the winter season

	CASCADES ISLAND

	12/27
	FG6-12 and

6-13
	Incorrect position for tailwater
	System in manual
	Operators adjusted.
	

	12/28
	CI entrance gates
	Incorrect position for tailwater
	System in manual
	Operators adjusted.
	

	12/28
	CI entrance differential
	<1.0’
	System in manual
	Operators adjusted.
	

	All week
	FG6-14
	½ open
	Electricians need to do some rewiring.
	Winter maintenance item.
	

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	WASHINGTON SHORE

	12/28
	PH2 Diffusers
	Incorrect position for tailwater
	In manual
	Operators adjusted.
	

	All week
	Weir 67
	Reading > 1.0’
	UMT closed.
	No action taken.
	

	All week
	WS velocity
	Meter reading <1.0
	Unknown- may be related to the low differential.
	Fisheries will monitor.
	


4.2.1 FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November 
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 28 December this week.  
4.5.2 BI was dewatered on 17 December.

4.5.3 Cascades Island fishway PLC is in manual.
4.5.4 The UMT remains closed.  Cascades Island exit remains open. 
4.5.5 PH2 FOG stab plates are installed as of 03 December due to Fish Unit 2 outage.
4.6 Juvenile Fishways.
4.6.1 DSM2 was dewatered on 19 December. 
4.6.2 DSM1 was dewatered on 20 December. 

4.7 Lamprey Fishways.  Winterized.
5 CONSTRUCTION
5.1 PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.
5.2 PH2 VBS mods.  Unit 14 modification is complete and Unit 18 is currently OOS.  U17 VBS monitoring equipment will be installed at this time as well.

5.3 TIE crane.  The TIE crane boom repair is on hold until funding is secured.
6 HAZMAT, SPILLS AND CLEANUP.  Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 20 December replaces the tail water operation for chum spawning teletype on 12 December.  Effective 0600 hours on Monday, December 24, until further notice, operate Bonneville tail water as follows – minimum 11.5 ft all hours.   The minimum 11.5 ft is for chum incubation.
JAMES R. MAHAR, P.E.

Operations Manager
1

