CENWP-OP-B                                                                                                                         January 7, 2008
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 01 of 2008, which covers the period from 30 December 2007 through 05 January 2008.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 115.7 to 160.6 kcfs.  Daily average project tailwater ranged from 12.1’ to 14.5’ msl.  Daily average powerhouse forebay elevation ranged from 74.3’ to 75.4’ msl.  Daily average river temperature ranged from 40° to 41°F.  Secchi disk measurements ranged from 4.5’ to 7.0.’
1.2 Spill Bay 1, which supplies attraction flow for Cascades Island, is included in the spill pattern.  Daily average spill ranged from 0.5 to 0.6 kcfs.
1.3 Unit Operation.   Powerhouse 2 is the priority powerhouse.
1.3.1 Unit 1 has remained out of service since 23 October due to governor trouble.
1.3.2 Unit 7 has remained out of service since 04 June for turbine rehab.

1.3.3 Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

1.3.4 Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.
1.3.5 Unit 18 has remained out of service since 03 December for FGE modifications and 4 year overhaul.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 Unit F1 was placed on standby from 0758 to 0835 on 02 January to rake trash.

1.4.2 Unit F2 has remained out of service since 03 December for exciter replacement.  

1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS valves were closed this reporting period: 
2.1.1 FV 1-1, 3-7, and 3-9 remain closed for winter maintenance in A-branch.

2.1.2 FV 4-3 and 4-4 remain closed for winter maintenance in B-branch.
2.1.3 FV 5-9 was closed for cleaning from 0836 to 0848 on 05 January.
2.2 STS/VBS Inspections.  No STS/VBS inspections occurred this week: 
Table 1.  STS and VBS inspections.  

	Unit
	Date
	Run Hours
	Comments

	3-4, 11-18
	NA
	NA
	All screens were pulled for winter maintenance.


2.3 Dewatering and Fish Salvage. 
2.3.1 The AFF was dewatered on 31 December.  One juvenile wild steelhead, one bluegill, and one sturgeon were removed.  All were released at the Hamilton Island boat ramp in good condition.
3 RESEARCH  
3.1 WDFW Fish Counting.  Video counting continues at Cascades Island and WA Shore.
4 FISHWAYS 

4.1 Project biologists inspected on 02-04 January.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES- OOS for the winter season

	CASCADES ISLAND

	All week
	FG6-14
	½ way open
	Electricians need to do some rewiring.
	Winter maintenance item.
	

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	WASHINGTON SHORE

	1/2
	Weir 37 and 38
	Reading >1.0’
	AFF dewatered
	Operators adjusted.
	

	All week
	Weir 67
	Reading > 1.0’
	UMT closed.
	No action taken.
	

	All week
	WS velocity
	Meter reading <1.0
	Unknown- may be related to the low differential.
	Fisheries will monitor.
	


4.2.1 FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November 
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 03 January this week.  
4.5.2 BI was dewatered on 17 December.

4.5.3 Cascades Island fishway PLC is in manual.
4.5.4 The UMT remains closed.  Cascades Island exit remains open. 
4.5.5 PH2 FOG stab plates are installed as of 03 December due to Fish Unit 2 outage.
4.5.6 The AFF was dewatered on 31 December.

4.6 Juvenile Fishways.
4.6.1 DSM 1 and 2 remain dewatered.
4.7 Lamprey Fishways.  Winterized.
5 CONSTRUCTION
5.1 PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.
5.2 PH2 VBS mods.  Unit 14 and 18 are currently OOS.  U17 VBS monitoring equipment will be installed at this time as well.

5.3 TIE crane.  The TIE crane boom repair is on hold until funding is secured.
6 HAZMAT, SPILLS AND CLEANUP.  Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 20 December replaces the tail water operation for chum spawning teletype on 12 December.  Effective 0600 hours on Monday, December 24, until further notice, operate Bonneville tail water as follows – minimum 11.5 ft all hours.   The minimum 11.5 ft is for chum incubation.
7.2 A teletype sent on 02 January requests a change in PH1 unit priority.  Unit 2 is to be operated on a last on, first off basis for approximately one month, due to an undiagnosed problem with the unit.

JAMES R. MAHAR, P.E.

Operations Manager
1

