CENWP-OP-B                                                                                                                         March 19, 2008
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 11 of 2008, which covers the period from 09 March through 15 March 2008.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 127.7 to 172.5 kcfs.  Daily average project tailwater ranged from 12.1’ to 15.3’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 75.3’ msl.  Daily average river temperature ranged from 42 - 43°F.  Secchi disk measurements ranged from 5.0 to 7.0.’
1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 1.4 to 35.1 kcfs.
1.3 Unit Operation.   Powerhouse 2 is the priority powerhouse.
1.3.1 Unit 7 has remained out of service since 04 June for turbine rehab.

1.3.2 Unit 8 has remained out of service since 12 September 2006 for turbine rehab.
1.3.3 Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.

1.3.4 Unit 16 has remained out of service since 05 March for FGE repairs in gatewell 16A.
1.3.5 Unit 17 has remained out of service since 23 February for FGE modifications.

1.3.6 Unit 18 was out of service from 0845 until 1257 on 10 March due to a governor control oil issue.  Was out of service from 1300 until 1400 on 13 March for Governor pressure regulator repairs.  
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS closures occurred this reporting week:

 2.1.1
   FV 1-1 was closed for cleaning from 1458 until 1530 on 10 March.  

2.2 STS/VBS Inspections.  No STS/VBS inspections occurred this reporting week.
Table 1.  STS and VBS inspections.  

	Unit
	Date
	Run Hours
	Comments

	11-18
	NA
	NA
	NA


2.3 Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this reporting week.
3 RESEARCH  
3.1 Battelle.  Monitoring with DIDSON acoustic camera and split-beam hydroacoustics near B2CC entrance to estimate the numbers and distribution of kelt sized targets. 
3.2 Fish Field Unit.  Pinniped observation and scat collection continue.

3.3 NOAA- Gilbreath.  Juvenile fish releases in gatewell 14A scheduled to begin the week of 17 March.  

3.4 PSMFC Smolt Monitoring. Index and condition sampling continues.
3.5 USDA Wildlife Services. Sea lion hazing from the powerhouses continues.

3.6 WDFW Fish Counting.  Video counting continues at Bradford Island and WA Shore.

3.7 WDFW/ODFW Sea lion hazing.  Hazing from boats continues.

4 FISHWAYS 

4.1 Project biologists inspected on 09-15 March.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES

	3/10
	B-branch entrance
	Differential > 2.0’
	System in manual
	Operators adjusted
	

	All week
	WG 64
	Incorrect position
	Brake seized
	Repairs to occur after navlock O/H
	

	CASCADES ISLAND- nothing to report

	
	
	
	
	
	

	WASHINGTON SHORE

	3/9
	DSM2 orifices
	Incorrect position
	Bad prox. switches
	
	08-28029/30

	3/9,12,14-15
	Weir 38
	Reading <1.0’
	Valve 2 winterized
	In criteria 3/19
	


4.2.1 FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 08/09.  It is only out of criteria when tailwater is above 19.0’ msl.
4.2.2 PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter often reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

4.2.3 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.
4.3.1 Bradford Island temperatures are not available at this time.  The Project is waiting on a new temperature probe.  The new probe should be installed by mid-April.

Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

 average

	3/09
	40.8
	NA

	3/10
	43.0
	NA

	3/11
	42.7
	NA

	3/12
	41.5
	NA

	3/13
	41.6
	NA

	3/14
	40.6
	NA

	3/15
	40.1
	NA


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 14 March.  
4.5.2 B-Branch and Cascades Island fishway PLC are in manual.
4.5.3 PH2 FOG (floating orifice gate) stab plates are installed as of 03 December.  FOG sea lion exclusion bars are scheduled for installation the week of 17 March.
4.5.4 SLEDs (sea lion exclusion devices) and acoustic deterrents are installed at all fishway entrances.
4.6 Juvenile Fishways.
4.6.1 B2CC was closed from 1250 until 1520 on 13 March to reposition kelt research equipment.
4.7 Lamprey Fishways.  Remain winterized.
5 CONSTRUCTION
5.1 PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.
5.2 PH2 VBS mods.  Unit 17 is currently OOS for installation of monitoring equipment.  Unit 16 is currently OOS for FGE repairs in gatewell 16A.
5.3 TIE crane.  The TIE crane boom repair is on hold until funding is secured.

5.4 BGS.  Re-alignment of the anchors is scheduled for the week of 17 March.
6 HAZMAT, SPILLS AND CLEANUP.  Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 20 December replaces the tail water operation for chum spawning teletype on 12 December.  Effective 0600 hours on Monday, December 24, until further notice, operate Bonneville tail water as follows – minimum 11.5 ft all hours.   The minimum 11.5 ft is for chum incubation.
7.2 A teletype sent on 06 March requests special Project operations, in support of the Spring Creek hatchery release of 3.75 million tule fall Chinook on 05 March and 06 March, from 2359 on 06 March until 0600 on 10 March: 

7.2.1 Spill approximately 36.4 kcfs.  Bays 1 and 18 will be open 0.5’.  Odd numbered bays 3-17 will be open 2’, even numbered bays will be on seal.
7.2.2 Spill operations will not exceed 120% total dissolved gas at Cascades Island and 115% at Camas/Washougal.

7.2.3 Maintain a minimum tailwater of 12.5’ to provide a TDG depth compensation level of 105% at Chum salmon redds.  A teletype sent on 07 March requested the minimum tailwater be maintained at 13.0’ as measured at Tanner Creek.
7.3 A teletype sent on 07 March requests special operations in support of the Spring Creek hatchery release.  From 0600 on 06 March until 0600 on 10 March, PH2 units will operate at the low end of the lower quarter point of the 1% best efficiency range.  PH2 is the priority powerhouse, if PH1 operates then MGR units will be first on/ last off, as outlined in the FPP, and within the 1% best efficiency range.  Teletypes sent on 10 and 13 March extend this operation until 1700 on 13 March.  Unit operation will return to 2008 FPP criteria.
7.4 A teletype sent on 13 March requests the closure of the B2CC from approximately 1200 to 1500 on 13 March.  This is necessary to reposition hydroacoustic transducers.
7.5 A teletype sent on 13 March requests the Bonneville forebay be restricted to the following elevations as a soft constraint from 1200-1700 on 22 March: 71.5’ - 73.0’.  This operation is to assist in beach cleanup at the Port of Hood River.

JAMES R. MAHAR, P.E.

Operations Manager
1

