CENWP-OP-B                                                                                                                         June 2, 2008
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 22 of 2008, which covers the period from 25 May through 31 May 2008.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 373.5 to 420.8 kcfs.  Daily average project tailwater ranged from 26.5’ to 28.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 74.4’ msl.  Daily average river temperature was 56°F.  Secchi disk measurements ranged from 2.9 to 3.0.’
1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 167.9 to 211.8 kcfs.
1.2.1 On 27 May, while opening Bay 15 to flush debris, the hoist failed and the gate fell to the sill.  It remains in the closed position leaving a hole in the spill pattern.
1.3 Unit Operation.  Powerhouse 2 is the priority powerhouse.
1.3.1 Unit 3 returned to service at 1438 on 30 May.  It had been out of service since 14 April for a five year overhaul.  U3 was out of service from 0820 until 0830 on 31 May for CT wiring checks.
1.3.2 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.3 Unit 8 has remained out of service since 12 September 2006 for turbine rehab.
1.3.4 Until 9 was out of service from 1445 until 2130 on 30 May for Unit 8 alignment.

1.3.5 Unit 11 was forced out of service from 1500 until 1717 due to the unit tripping.  U11 was out of service from 1242 until 1610 on 28 May for STS installation and trashrack raking.  U11 was out of service from 1609 until 1742 on 29 May for STS removal.
1.3.6 Unit 12 was out of service from 0959 until 1023 on 29 May for trashrack raking.
1.3.7 Unit 13 was out of service from 0854 until 0920 on 29 May for trashrack raking.
1.3.8 Unit 14 was out of service from 0822 until 0852 on 29 May for trashrack raking.
1.3.9 Unit 15 has remained out of service since 25 November 2007due to exciter and pole failure, followed by a head gate hydraulic line rupture.

1.3.10 Unit 16 was out of service from 1613 until 1642 on 28 May for trashrack raking.
1.3.11 Unit 17 was out of service from 0648 until 0742 on 29 May for trashrack raking.
1.3.12 Unit 18 was out of service from 0702 until 0718 on 27 May for packing adjustments.  U18 was out of service from 0746 until 0819 on 29 May for trashrack raking.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
1.5.1 On 14 May, operators discovered the VBS sensors were reading low by 0.1’-0.5’.  All sensors were calibrated by 21 May.  Additional errors in calibration were found.  The control room continues to check VBS differential manually.
2 ACTIVITIES

2.1 AWS Closures.  The following AWS closures occurred this reporting week:
2.1.1 FV 1-1 was closed to float trash from 2200 until 0400 on 24-27 May, from 0020 until 0420 on 28 May, and from 2142 on 31 May until 0504 on 01 June.
2.1.2 FV 3-7 was closed for cleaning from 0706 until 0748 on 27 May.  FV 3-7 was closed to float trash from 2200 until 0400 on 24-27 May, from 0020 until 0420 on 28 May, and from 2142 on 31 May until 0504 on 01 June.
2.1.3 FV3-9 was closed for cleaning from 0651 until 0748 on 27 May.

2.1.4 FV5-9 was closed for cleaning from 1023 until 1307 on 27 May.

2.1.5 FV6-9 was closed for cleaning from 0857 until 0916 on 27 May and from 1053 until 1105 on 29 May.

2.2 STS/VBS Inspections.  STS/VBS inspections were scheduled for the week of 18 May.  Instead, STSs were pulled due to high flows and debris loads.
Table 1.  STS and VBS inspections.  

	Unit
	Date
	Run Hours
	Comments

	11-18
	NA
	NA
	STSs removed.


2.3 Dewatering and Fish Salvage. The following fish salvage activities occurred this reporting week:
2.3.1 Nine sculpin, one catfish, and two Chinook smolts were recovered from U3 tail logs on 29 May.  The smolts were mortalities.
3 RESEARCH  
3.1 Battelle.  BGS hydrophones are installed.
3.2 Battelle.  Equipment installation completed for a spillway survival evaluation.
3.3 CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF began 15 April.

3.4 Fish Field Unit.  Pinniped observations concluded on 31 May.

3.5 NOAA – Gilbreath.  No releases occurred this week due to STS removal.    
3.6 NOAA – Jacobson.  Collected 25 chinook and 25 coho from PSMFC for pathogen testing. 

3.7 NOAA – McComas.  Collected 482 chinook from PSMFC for JSATS and PIT tag testing.
3.8 NOAA – Pennington.  Lamprey ramps remain in service.  No collection at WS NDE due to TW elevation (platform is at or under water).  Traps in the AFF are deployed at night.
3.9 PSMFC Smolt Monitoring.  Ten steelhead, four salmon, and one unidentified salmonid were recorded crossing the separator bars.  GBT results may be found at http://www.fpc.org/CurrentDaily/Gbtsum.txt.  507 yearling chinook and 25 coho were held for NOAA researchers, 84 yearling chinook were collected for Univ. of WA.
3.10 USDA Wildlife Services. Sea lion hazing concluded on May 20th.  Avian hazing continues.
3.11 University of Washington.  Collection of barged fish, SbyC, and RoR fish for challenge trial continues.   Collected 84 chinook from PSMFC.
3.12 WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.
4 FISHWAYS 

4.1 Project biologists inspected on 25 – 31 May.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND AND BRANCHES

	All week
	FG3-5
	Closed.
	Diffuser broken.
	See 4.2.4
	08-38527

	5/28-30
	A-branch weir
	Reading >1.3’
	Unknown
	No action.
	

	All week
	B-branch weir
	Reading >1.3’ or underwater
	High TW
	No action.
	

	5/29
	B-branch diffusers
	Incorrect position for TW elev.
	System in manual.
	Ops adjusted.
	

	5/27-5/31
	Spillbay 15
	Gate on seal
	Hoist failure
	
	

	CASCADES ISLAND

	5/27
	UMT weir
	Reading < 1.3’
	Unknown
	
	

	All week
	FG6-10
	Closed.
	Diffuser broken
	See 4.2.1
	

	5/29
	CI diffusers
	Incorrect position for TW elev.
	System in manual.
	Ops adjusted.
	

	5/30
	CI entrance
	Differential >2.0’
	System in manual.
	Ops adjusted.
	

	WASHINGTON SHORE

	All week
	PH2 
	STSs pulled
	High debris loads
	
	

	All week
	DSM2 airburst
	Operating incorrectly
	PLC issues.
	
	08-37503


4.2.1 FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 09/10.  It is OOC when TW is above 19.0’ msl.
4.2.2 PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

4.2.3 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.2.4 FG3-5 closed.  The shaft and gate have parted ways.  Repairs scheduled for winter 09/10.  It’s OOC at TW 16.7’ msl and higher.

4.2.5 PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will not be made until winter 08/09.

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

4.3.1 BI temperatures are not available at this time.   The new probe is installed but not yet programmed.
4.3.2 The WS fishway temperature probe is no longer working properly.  Replacement and/or repairs are expected to take a couple of months.  Until then, the AFF probe will be used as a surrogate.
Table 3.  Bonneville Fishway Temperatures

	Date
	WS average
	AFF 
	BI average

	5/25
	NA
	55.6
	NA

	5/26
	NA
	55.3
	NA

	5/27
	NA
	55.8
	NA

	5/28
	NA
	55.8
	NA

	5/29
	NA
	54.2
	NA

	5/30
	NA
	54.7
	NA

	5/31
	NA
	55.3
	NA


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 31 May.
4.5.2 B-Branch and Cascades Island fishway PLC are in manual.
4.5.3 Installation of the FOG sea lion exclusion bars has halted due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.  
4.5.4 SLEDs and acoustic deterrents remain installed at fishway entrances.
4.5.5 Fishways went to shad passage mode on 15 May.

4.5.6 FV1-1 and FV3-7 were closed at night throughout the week to float debris off the trashracks.  
4.6 Juvenile Fishways.

4.6.1 F2 south orifices were closed from 0040 on 27 May until 0005 on 29 May maintain DSM2 elevations.
4.6.2 U11 orifices were closed at 1349 on 28 May for STS installation.
4.6.3 On 21 May, a regional decision was made to pull STSs.  STSs were pulled from 21 – 23 May.  Unit 11 STSs were installed on 28 May to monitor debris accumulation on the VBSs.  Due to high VBS drawdowns after roughly 24 hours, U11 STSs were removed.
4.7 Lamprey Fishways.  
4.7.1 BI and WS AWS lamprey ramps remain in service.
4.7.2 The WS NDE lamprey ramp remained deployed.
5 CONSTRUCTION
5.1 PH1 ITS Wall Removal.  Three automated gates to be installed.  May slope the floor and remove the wall.
5.2 TIE crane.  The TIE crane boom repair is on hold until funding is secured.

6 HAZMAT, SPILLS AND CLEANUP. 
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 10 April requests the Project to begin juvenile fish spill beginning at 0001 on 10 April and continuing until further notice.  Spill will be 100Kcfs/ 24 hrs a day.  The current pattern can be found in the 2008 FPP at www.nwd-wc.usace.army.mil/tmt/documents/fpp/
7.2 A teletype sent on 14 May requests U14 be operated as first priority from 1200 on 14 May until 1800 on 18 May to accommodate the NOAA gatewell tests.  A 20 May teletype extended the U14 operation from 1200 on 21 May until 1800 on 25 May.
7.3 A teletype sent on 21 May authorizes the Project remove PH2 STSs and operate the units at the upper end of the 1% efficiency band.  This action is required due to the high flows and debris building up on the VBSs and fishway trashracks. 
7.4 A teletype sent on 27 May authorizes the Project to flush debris from spillbays 1, 2, 15, 16, 17, and 18 to prevent damage to research equipment.
7.5 A teletype sent on 28 May requests the project reinstall STSs in Unit 11 to determine if debris load has declined to a manageable level.
7.6 A teletype sent on 29 May authorizes the Project to remove the STSs from Unit 11 due to excessive debris buildup.

JAMES R. MAHAR, P.E.

Operations Manager
1

